## techniques
ID | STIX ID | name | description | url | created | last modified | domain | version | tactics | detection | platforms | data sources | contributors | relationship citations
T0800 | attack-pattern--19a71d1e-6334-4233-8260-b749cae37953 | Activate Firmware Update Mode | Adversaries may activate firmware update mode on devices to prevent expected response functions from engaging in reaction to an emergency or process malfunction. For example, devices such as protection relays may have an operation mode designed for firmware installation. This mode may halt process monitoring and related functions to allow new firmware to be loaded. A device left in update mode may be placed in an inactive holding state if no firmware is provided to it. By entering and leaving a device in this mode, the adversary may deny its usual functionalities. | https://attack.mitre.org/techniques/T0800 | 21 May 2020 | 13 October 2023 | ics-attack | 1.0 | Inhibit Response Function |  | None | Application Log: Application Log Content, Network Traffic: Network Traffic Content, Operational Databases: Device Alarm | Joe Slowik - Dragos | (Citation: Joe Slowik August 2019),(Citation: Department of Homeland Security September 2016),
T0830 | attack-pattern--9a505987-ab05-4f46-a9a6-6441442eec3b | Adversary-in-the-Middle | Adversaries with privileged network access may seek to modify network traffic in real time using adversary-in-the-middle (AiTM) attacks. (Citation: Gabriel Sanchez October 2017) This type of attack allows the adversary to intercept traffic to and/or from a particular device on the network. If a AiTM attack is established, then the adversary has the ability to block, log, modify, or inject traffic into the communication stream. There are several ways to accomplish this attack, but some of the most-common are Address Resolution Protocol (ARP) poisoning and the use of a proxy. (Citation: Bonnie Zhu, Anthony Joseph, Shankar Sastry 2011) An AiTM attack may allow an adversary to perform the following attacks: [Block Reporting Message](https://attack.mitre.org/techniques/T0804), [Spoof Reporting Message](https://attack.mitre.org/techniques/T0856), [Modify Parameter](https://attack.mitre.org/techniques/T0836), [Unauthorized Command Message](https://attack.mitre.org/techniques/T0855) | https://attack.mitre.org/techniques/T0830 | 21 May 2020 | 13 October 2023 | ics-attack | 2.0 | Collection |  | None | Application Log: Application Log Content, Network Traffic: Network Traffic Content, Network Traffic: Network Traffic Flow, Process: Process Creation, Service: Service Creation, Windows Registry: Windows Registry Key Modification | Conrad Layne - GE Digital | (Citation: Carl Hurd March 2019),(Citation: William Largent June 2018),(Citation: Triton-EENews-2017),,
T0878 | attack-pattern--2900bbd8-308a-4274-b074-5b8bde8347bc | Alarm Suppression | Adversaries may target protection function alarms to prevent them from notifying operators of critical conditions. Alarm messages may be a part of an overall reporting system and of particular interest for adversaries. Disruption of the alarm system does not imply the disruption of the reporting system as a whole. A Secura presentation on targeting OT notes a dual fold goal for adversaries attempting alarm suppression: prevent outgoing alarms from being raised and prevent incoming alarms from being responded to. (Citation: Jos Wetzels, Marina Krotofil 2019) The method of suppression may greatly depend on the type of alarm in question: * An alarm raised by a protocol message * An alarm signaled with I/O * An alarm bit set in a flag (and read) In ICS environments, the adversary may have to suppress or contend with multiple alarms and/or alarm propagation to achieve a specific goal to evade detection or prevent intended responses from occurring. (Citation: Jos Wetzels, Marina Krotofil 2019) Methods of suppression may involve tampering or altering device displays and logs, modifying in memory code to fixed values, or even tampering with assembly level instruction code. | https://attack.mitre.org/techniques/T0878 | 21 May 2020 | 13 October 2023 | ics-attack | 1.2 | Inhibit Response Function |  | None | Network Traffic: Network Traffic Flow, Operational Databases: Device Alarm, Operational Databases: Process History/Live Data, Operational Databases: Process/Event Alarm | Jos Wetzels - Midnight Blue; Marina Krotofil | (Citation: Marshall Abrams July 2008),(Citation: Dwight Anderson 2014),(Citation: Karen Scarfone; Paul Hoffman September 2009),(Citation: Department of Homeland Security September 2016),(Citation: Keith Stouffer May 2015),
T0802 | attack-pattern--3de230d4-3e42-4041-b089-17e1128feded | Automated Collection | Adversaries may automate collection of industrial environment information using tools or scripts. This automated collection may leverage native control protocols and tools available in the control systems environment. For example, the OPC protocol may be used to enumerate and gather information. Access to a system or interface with these native protocols may allow collection and enumeration of other attached, communicating servers and devices. | https://attack.mitre.org/techniques/T0802 | 21 May 2020 | 05 April 2024 | ics-attack | 1.1 | Collection |  | None | Command: Command Execution, File: File Access, Network Traffic: Network Traffic Content, Script: Script Execution |  | (Citation: Anton Cherepanov, ESET June 2017),(Citation: Daavid Hentunen, Antti Tikkanen June 2014),(Citation: Industroyer2 Forescout July 2022),,
T0895 | attack-pattern--77d9c726-b53e-481d-8bcc-1068aebfbb9d | Autorun Image | Adversaries may leverage AutoRun functionality or scripts to execute malicious code. Devices configured to enable AutoRun functionality or legacy operating systems may be susceptible to abuse of these features to run malicious code stored on various forms of removeable media (i.e., USB, Disk Images [.ISO]). Commonly, AutoRun or AutoPlay are disabled in many operating systems configurations to mitigate against this technique. If a device is configured to enable AutoRun or AutoPlay, adversaries may execute code on the device by mounting the removable media to the device, either through physical or virtual means. This may be especially relevant for virtual machine environments where disk images may be dynamically mapped to a guest system on a hypervisor. An example could include an adversary gaining access to a hypervisor through the management interface to modify a virtual machine’s hardware configuration. They could then deploy an iso image with a malicious AutoRun script to cause the virtual machine to automatically execute the code contained on the disk image. This would enable the execution of malicious code within a virtual machine without needing any prior remote access to that system. | https://attack.mitre.org/techniques/T0895 | 26 March 2024 | 08 April 2024 | ics-attack | 1.0 | Execution |  |  | Drive: Drive Creation, Process: Process Creation |  | (Citation: Mandiant-Sandworm-Ukraine-2022),,
T0803 | attack-pattern--008b8f56-6107-48be-aa9f-746f927dbb61 | Block Command Message | Adversaries may block a command message from reaching its intended target to prevent command execution. In OT networks, command messages are sent to provide instructions to control system devices. A blocked command message can inhibit response functions from correcting a disruption or unsafe condition. (Citation: Bonnie Zhu, Anthony Joseph, Shankar Sastry 2011) (Citation: Electricity Information Sharing and Analysis Center; SANS Industrial Control Systems March 2016) | https://attack.mitre.org/techniques/T0803 | 21 May 2020 | 13 October 2023 | ics-attack | 1.1 | Inhibit Response Function |  | None | Application Log: Application Log Content, Network Traffic: Network Traffic Flow, Operational Databases: Process History/Live Data, Operational Databases: Process/Event Alarm, Process: Process Termination |  | (Citation: Anton Cherepanov, ESET June 2017),(Citation: Ukraine15 - EISAC - 201603),,
T0804 | attack-pattern--3f1f4ccb-9be2-4ff8-8f69-dd972221169b | Block Reporting Message | Adversaries may block or prevent a reporting message from reaching its intended target. In control systems, reporting messages contain telemetry data (e.g., I/O values) pertaining to the current state of equipment and the industrial process. By blocking these reporting messages, an adversary can potentially hide their actions from an operator. Blocking reporting messages in control systems that manage physical processes may contribute to system impact, causing inhibition of a response function. A control system may not be able to respond in a proper or timely manner to an event, such as a dangerous fault, if its corresponding reporting message is blocked. (Citation: Bonnie Zhu, Anthony Joseph, Shankar Sastry 2011) (Citation: Electricity Information Sharing and Analysis Center; SANS Industrial Control Systems March 2016) | https://attack.mitre.org/techniques/T0804 | 21 May 2020 | 13 October 2023 | ics-attack | 1.0 | Inhibit Response Function |  | None | Application Log: Application Log Content, Network Traffic: Network Traffic Flow, Operational Databases: Process History/Live Data, Operational Databases: Process/Event Alarm, Process: Process Termination |  | (Citation: Anton Cherepanov, ESET June 2017),(Citation: Ukraine15 - EISAC - 201603),,
T0805 | attack-pattern--1c478716-71d9-46a4-9a53-fa5d576adb60 | Block Serial COM | Adversaries may block access to serial COM to prevent instructions or configurations from reaching target devices. Serial Communication ports (COM) allow communication with control system devices. Devices can receive command and configuration messages over such serial COM. Devices also use serial COM to send command and reporting messages. Blocking device serial COM may also block command messages and block reporting messages. A serial to Ethernet converter is often connected to a serial COM to facilitate communication between serial and Ethernet devices. One approach to blocking a serial COM would be to create and hold open a TCP session with the Ethernet side of the converter. A serial to Ethernet converter may have a few ports open to facilitate multiple communications. For example, if there are three serial COM available -- 1, 2 and 3 --, the converter might be listening on the corresponding ports 20001, 20002, and 20003. If a TCP/IP connection is opened with one of these ports and held open, then the port will be unavailable for use by another party. One way the adversary could achieve this would be to initiate a TCP session with the serial to Ethernet converter at 10.0.0.1 via Telnet on serial port 1 with the following command: telnet 10.0.0.1 20001. | https://attack.mitre.org/techniques/T0805 | 21 May 2020 | 13 October 2023 | ics-attack | 1.1 | Inhibit Response Function |  | None | Application Log: Application Log Content, Network Traffic: Network Traffic Flow, Operational Databases: Process History/Live Data, Operational Databases: Process/Event Alarm, Process: Process Termination |  | (Citation: Anton Cherepanov, ESET June 2017),(Citation: Booz Allen Hamilton),,
T0806 | attack-pattern--8e7089d3-fba2-44f8-94a8-9a79c53920c4 | Brute Force I/O | Adversaries may repetitively or successively change I/O point values to perform an action. Brute Force I/O may be achieved by changing either a range of I/O point values or a single point value repeatedly to manipulate a process function. The adversary's goal and the information they have about the target environment will influence which of the options they choose. In the case of brute forcing a range of point values, the adversary may be able to achieve an impact without targeting a specific point. In the case where a single point is targeted, the adversary may be able to generate instability on the process function associated with that particular point. Adversaries may use Brute Force I/O to cause failures within various industrial processes. These failures could be the result of wear on equipment or damage to downstream equipment. | https://attack.mitre.org/techniques/T0806 | 21 May 2020 | 13 October 2023 | ics-attack | 1.1 | Impair Process Control |  | None | Application Log: Application Log Content, Network Traffic: Network Traffic Content, Operational Databases: Process History/Live Data |  | (Citation: Anton Cherepanov, ESET June 2017),(Citation: Claroty Fuxnet 2024),(Citation: Industroyer2 Mandiant April 2022),(Citation: Industroyer2 Forescout July 2022),(Citation: Dwight Anderson 2014),(Citation: Karen Scarfone; Paul Hoffman September 2009),(Citation: Department of Homeland Security September 2016),(Citation: Keith Stouffer May 2015),
T0892 | attack-pattern--fab8fc7d-f27f-4fbb-9de6-44740aade05f | Change Credential | Adversaries may modify software and device credentials to prevent operator and responder access. Depending on the device, the modification or addition of this password could prevent any device configuration actions from being accomplished and may require a factory reset or replacement of hardware. These credentials are often built-in features provided by the device vendors as a means to restrict access to management interfaces. An adversary with access to valid or hardcoded credentials could change the credential to prevent future authorized device access. Change Credential may be especially damaging when paired with other techniques such as Modify Program, Data Destruction, or Modify Controller Tasking. In these cases, a device’s configuration may be destroyed or include malicious actions for the process environment, which cannot not be removed through normal device configuration actions. Additionally, recovery of the device and original configuration may be difficult depending on the features provided by the device. In some cases, these passwords cannot be removed onsite and may require that the device be sent back to the vendor for additional recovery steps. A chain of incidents occurred in Germany, where adversaries locked operators out of their building automation system (BAS) controllers by enabling a previously unset BCU key. (Citation: German BAS Lockout Dec 2021) | https://attack.mitre.org/techniques/T0892 | 30 March 2023 | 13 October 2023 | ics-attack | 1.0 | Inhibit Response Function |  | None | Network Traffic: Network Traffic Content, Operational Databases: Device Alarm | Felix Eberstaller | ,(Citation: Department of Homeland Security October 2009),(Citation: M. Rentschler and H. Heine),(Citation: CISA June 2013),
T0858 | attack-pattern--2883c520-7957-46ca-89bd-dab1ad53b601 | Change Operating Mode | Adversaries may change the operating mode of a controller to gain additional access to engineering functions such as Program Download. Programmable controllers typically have several modes of operation that control the state of the user program and control access to the controllers API. Operating modes can be physically selected using a key switch on the face of the controller but may also be selected with calls to the controllers API. Operating modes and the mechanisms by which they are selected often vary by vendor and product line. Some commonly implemented operating modes are described below: * Program - This mode must be enabled before changes can be made to a devices program. This allows program uploads and downloads between the device and an engineering workstation. Often the PLCs logic Is halted, and all outputs may be forced off. (Citation: N.A. October 2017) * Run - Execution of the devices program occurs in this mode. Input and output (values, points, tags, elements, etc.) are monitored and used according to the programs logic. [Program Upload](https://attack.mitre.org/techniques/T0845) and [Program Download](https://attack.mitre.org/techniques/T0843) are disabled while in this mode. (Citation: Omron) (Citation: Machine Information Systems 2007) (Citation: N.A. October 2017) (Citation: PLCgurus 2021) * Remote - Allows for remote changes to a PLCs operation mode. (Citation: PLCgurus 2021) * Stop - The PLC and program is stopped, while in this mode, outputs are forced off. (Citation: Machine Information Systems 2007) * Reset - Conditions on the PLC are reset to their original states. Warm resets may retain some memory while cold resets will reset all I/O and data registers. (Citation: Machine Information Systems 2007) * Test / Monitor mode - Similar to run mode, I/O is processed, although this mode allows for monitoring, force set, resets, and more generally tuning or debugging of the system. Often monitor mode may be used as a trial for initialization. (Citation: Omron) | https://attack.mitre.org/techniques/T0858 | 21 May 2020 | 13 October 2023 | ics-attack | 1.0 | Evasion, Execution |  | None | Application Log: Application Log Content, Network Traffic: Network Traffic Content, Operational Databases: Device Alarm |  | (Citation: Spenneberg, Ralf, Maik Brggemann, and Hendrik Schwartke March 2016),(Citation: Wylie-22),(Citation: MDudek-ICS),(Citation: Dragos-Pipedream),(Citation: Department of Homeland Security September 2016),
T0807 | attack-pattern--24a9253e-8948-4c98-b751-8e2aee53127c | Command-Line Interface | Adversaries may utilize command-line interfaces (CLIs) to interact with systems and execute commands. CLIs provide a means of interacting with computer systems and are a common feature across many types of platforms and devices within control systems environments. (Citation: Enterprise ATT&CK January 2018) Adversaries may also use CLIs to install and run new software, including malicious tools that may be installed over the course of an operation. CLIs are typically accessed locally, but can also be exposed via services, such as SSH, Telnet, and RDP. Commands that are executed in the CLI execute with the current permissions level of the process running the terminal emulator, unless the command specifies a change in permissions context. Many controllers have CLI interfaces for management purposes. | https://attack.mitre.org/techniques/T0807 | 21 May 2020 | 13 October 2023 | ics-attack | 1.1 | Execution |  | None | Application Log: Application Log Content, Command: Command Execution, Process: Process Creation |  | (Citation: Anton Cherepanov, ESET June 2017),(Citation: Nicolas Falliere, Liam O Murchu, Eric Chien February 2011),(Citation: ESET Industroyer),(Citation: FireEye TRITON Dec 2017),(Citation: Mandiant-Sandworm-Ukraine-2022),(Citation: Dragos October 2018),,
T0885 | attack-pattern--e6c31185-8040-4267-83d3-b217b8a92f07 | Commonly Used Port | Adversaries may communicate over a commonly used port to bypass firewalls or network detection systems and to blend in with normal network activity, to avoid more detailed inspection. They may use the protocol associated with the port, or a completely different protocol. They may use commonly open ports, such as the examples provided below. * TCP:80 (HTTP) * TCP:443 (HTTPS) * TCP/UDP:53 (DNS) * TCP:1024-4999 (OPC on XP/Win2k3) * TCP:49152-65535 (OPC on Vista and later) * TCP:23 (TELNET) * UDP:161 (SNMP) * TCP:502 (MODBUS) * TCP:102 (S7comm/ISO-TSAP) * TCP:20000 (DNP3) * TCP:44818 (Ethernet/IP) | https://attack.mitre.org/techniques/T0885 | 21 May 2020 | 13 October 2023 | ics-attack | 1.1 | Command and Control |  | None | Network Traffic: Network Traffic Content, Network Traffic: Network Traffic Flow | Matan Dobrushin - Otorio | (Citation: Nicolas Falliere, Liam O Murchu, Eric Chien February 2011),(Citation: MDudek-ICS),(Citation: Booz Allen Hamilton),(Citation: Gardiner, J., Cova, M., Nagaraja, S February 2014),
T0884 | attack-pattern--d67adac8-e3b9-44f9-9e6d-6c2a7d69dbe4 | Connection Proxy | Adversaries may use a connection proxy to direct network traffic between systems or act as an intermediary for network communications. The definition of a proxy can also be expanded to encompass trust relationships between networks in peer-to-peer, mesh, or trusted connections between networks consisting of hosts or systems that regularly communicate with each other. The network may be within a single organization or across multiple organizations with trust relationships. Adversaries could use these types of relationships to manage command and control communications, to reduce the number of simultaneous outbound network connections, to provide resiliency in the face of connection loss, or to ride over existing trusted communications paths between victims to avoid suspicion. (Citation: Enterprise ATT&CK January 2018) | https://attack.mitre.org/techniques/T0884 | 21 May 2020 | 13 October 2023 | ics-attack | 1.1 | Command and Control |  | None | Network Traffic: Network Traffic Content, Network Traffic: Network Traffic Flow |  | (Citation: Wylie-22),(Citation: Dragos Inc. June 2017),(Citation: Booz Allen Hamilton),(Citation: Gardiner, J., Cova, M., Nagaraja, S February 2014),
T0879 | attack-pattern--83ebd22f-b401-4d59-8219-2294172cf916 | Damage to Property | Adversaries may cause damage and destruction of property to infrastructure, equipment, and the surrounding environment when attacking control systems. This technique may result in device and operational equipment breakdown, or represent tangential damage from other techniques used in an attack. Depending on the severity of physical damage and disruption caused to control processes and systems, this technique may result in [Loss of Safety](https://attack.mitre.org/techniques/T0880). Operations that result in [Loss of Control](https://attack.mitre.org/techniques/T0827) may also cause damage to property, which may be directly or indirectly motivated by an adversary seeking to cause impact in the form of [Loss of Productivity and Revenue](https://attack.mitre.org/techniques/T0828). The German Federal Office for Information Security (BSI) reported a targeted attack on a steel mill under an incidents affecting business section of its 2014 IT Security Report. (Citation: BSI State of IT Security 2014) These targeted attacks affected industrial operations and resulted in breakdowns of control system components and even entire installations. As a result of these breakdowns, massive impact and damage resulted from the uncontrolled shutdown of a blast furnace. A Polish student used a remote controller device to interface with the Lodz city tram system in Poland. (Citation: John Bill May 2017) (Citation: Shelley Smith February 2008) (Citation: Bruce Schneier January 2008) Using this remote, the student was able to capture and replay legitimate tram signals. This resulted in damage to impacted trams, people, and the surrounding property. Reportedly, four trams were derailed and were forced to make emergency stops. (Citation: Shelley Smith February 2008) Commands issued by the student may have also resulted in tram collisions, causing harm to those on board and the environment outside. (Citation: Bruce Schneier January 2008) | https://attack.mitre.org/techniques/T0879 | 21 May 2020 | 13 October 2023 | ics-attack | 1.1 | Impact |  | None |  |  | (Citation: Marshall Abrams July 2008),(Citation: A G Foord, W G Gulland, C R Howard, T Kellacher, W H Smith 2004),(Citation: Department of Homeland Security September 2016),
T0809 | attack-pattern--493832d9-cea6-4b63-abe7-9a65a6473675 | Data Destruction | Adversaries may perform data destruction over the course of an operation. The adversary may drop or create malware, tools, or other non-native files on a target system to accomplish this, potentially leaving behind traces of malicious activities. Such non-native files and other data may be removed over the course of an intrusion to maintain a small footprint or as a standard part of the post-intrusion cleanup process. (Citation: Enterprise ATT&CK January 2018) Data destruction may also be used to render operator interfaces unable to respond and to disrupt response functions from occurring as expected. An adversary may also destroy data backups that are vital to recovery after an incident. Standard file deletion commands are available on most operating system and device interfaces to perform cleanup, but adversaries may use other tools as well. Two examples are Windows Sysinternals SDelete and Active@ Killdisk. | https://attack.mitre.org/techniques/T0809 | 21 May 2020 | 13 October 2023 | ics-attack | 1.0 | Inhibit Response Function |  | None | Command: Command Execution, File: File Deletion, File: File Modification, Process: Process Creation | Matan Dobrushin - Otorio | (Citation: Dragos Inc. June 2017),(Citation: Claroty Fuxnet 2024),(Citation: Brubaker-Incontroller),(Citation: Anton Cherepanov),(Citation: Wylie-22),(Citation: Dragos-Pipedream),(Citation: National Institute of Standards and Technology April 2013),
T0811 | attack-pattern--3405891b-16aa-4bd7-bd7c-733501f9b20f | Data from Information Repositories | Adversaries may target and collect data from information repositories. This can include sensitive data such as specifications, schematics, or diagrams of control system layouts, devices, and processes. Examples of information repositories include reference databases in the process environment, as well as databases in the corporate network that might contain information about the ICS.(Citation: Cybersecurity & Infrastructure Security Agency March 2018) Information collected from these systems may provide the adversary with a better understanding of the operational environment, vendors used, processes, or procedures of the ICS. In a campaign between 2011 and 2013 against ONG organizations, Chinese state-sponsored actors searched document repositories for specific information such as, system manuals, remote terminal unit (RTU) sites, personnel lists, documents that included the string SCAD*, user credentials, and remote dial-up access information. (Citation: CISA AA21-201A Pipeline Intrusion July 2021) | https://attack.mitre.org/techniques/T0811 | 21 May 2020 | 13 October 2023 | ics-attack | 1.2 | Collection |  | None | Application Log: Application Log Content, Logon Session: Logon Session Creation, Network Share: Network Share Access |  | (Citation: Symantec),(Citation: National Institute of Standards and Technology April 2013),(Citation: Keith Stouffer May 2015),
T0893 | attack-pattern--fa3aa267-da22-4bdd-961f-03223322a8d5 | Data from Local System | Adversaries may target and collect data from local system sources, such as file systems, configuration files, or local databases. This can include sensitive data such as specifications, schematics, or diagrams of control system layouts, devices, and processes. Adversaries may do this using [Command-Line Interface](https://attack.mitre.org/techniques/T0807) or [Scripting](https://attack.mitre.org/techniques/T0853) techniques to interact with the file system to gather information. Adversaries may also use [Automated Collection](https://attack.mitre.org/techniques/T0802) on the local system. | https://attack.mitre.org/techniques/T0893 | 30 March 2023 | 09 April 2024 | ics-attack | 1.0 | Collection |  | None | Command: Command Execution, File: File Access, Process: OS API Execution, Process: Process Creation, Script: Script Execution |  | (Citation: Kevin Savage and Branko Spasojevic),(Citation: ESET),(Citation: Symantec),(Citation: National Institute of Standards and Technology April 2013),(Citation: Keith Stouffer May 2015),
T0812 | attack-pattern--8bb4538f-f16f-49f0-a431-70b5444c7349 | Default Credentials | Adversaries may leverage manufacturer or supplier set default credentials on control system devices. These default credentials may have administrative permissions and may be necessary for initial configuration of the device. It is general best practice to change the passwords for these accounts as soon as possible, but some manufacturers may have devices that have passwords or usernames that cannot be changed. (Citation: Keith Stouffer May 2015) Default credentials are normally documented in an instruction manual that is either packaged with the device, published online through official means, or published online through unofficial means. Adversaries may leverage default credentials that have not been properly modified or disabled. | https://attack.mitre.org/techniques/T0812 | 21 May 2020 | 13 October 2023 | ics-attack | 1.0 | Lateral Movement |  | None | Logon Session: Logon Session Creation, Network Traffic: Network Traffic Content |  | (Citation: CISA Unitronics November 2023),(Citation: CISA AA23-335A IRGC-Affiliated December 2023),,
T0813 | attack-pattern--e33c7ecc-5a38-497f-beb2-a9a2049a4c20 | Denial of Control | Adversaries may cause a denial of control to temporarily prevent operators and engineers from interacting with process controls. An adversary may attempt to deny process control access to cause a temporary loss of communication with the control device or to prevent operator adjustment of process controls. An affected process may still be operating during the period of control loss, but not necessarily in a desired state. (Citation: Corero) (Citation: Michael J. Assante and Robert M. Lee) (Citation: Tyson Macaulay) In the 2017 Dallas Siren incident operators were unable to disable the false alarms from the Office of Emergency Management headquarters. (Citation: Mark Loveless April 2017) | https://attack.mitre.org/techniques/T0813 | 21 May 2020 | 13 October 2023 | ics-attack | 1.1 | Impact |  | None |  |  | (Citation: Anton Cherepanov, ESET June 2017),(Citation: Marshall Abrams July 2008),(Citation: Ukraine15 - EISAC - 201603),(Citation: Booz Allen Hamilton),(Citation: Department of Homeland Security October 2009),(Citation: National Institute of Standards and Technology April 2013),(Citation: M. Rentschler and H. Heine),
T0814 | attack-pattern--1b22b676-9347-4c55-9a35-ef0dc653db5b | Denial of Service | Adversaries may perform Denial-of-Service (DoS) attacks to disrupt expected device functionality. Examples of DoS attacks include overwhelming the target device with a high volume of requests in a short time period and sending the target device a request it does not know how to handle. Disrupting device state may temporarily render it unresponsive, possibly lasting until a reboot can occur. When placed in this state, devices may be unable to send and receive requests, and may not perform expected response functions in reaction to other events in the environment. Some ICS devices are particularly sensitive to DoS events, and may become unresponsive in reaction to even a simple ping sweep. Adversaries may also attempt to execute a Permanent Denial-of-Service (PDoS) against certain devices, such as in the case of the BrickerBot malware. (Citation: ICS-CERT April 2017) Adversaries may exploit a software vulnerability to cause a denial of service by taking advantage of a programming error in a program, service, or within the operating system software or kernel itself to execute adversary-controlled code. Vulnerabilities may exist in software that can be used to cause a denial of service condition. Adversaries may have prior knowledge about industrial protocols or control devices used in the environment through [Remote System Information Discovery](https://attack.mitre.org/techniques/T0888). There are examples of adversaries remotely causing a [Device Restart/Shutdown](https://attack.mitre.org/techniques/T0816) by exploiting a vulnerability that induces uncontrolled resource consumption. (Citation: ICS-CERT August 2018) (Citation: Common Weakness Enumeration January 2019) (Citation: MITRE March 2018) | https://attack.mitre.org/techniques/T0814 | 21 May 2020 | 14 October 2024 | ics-attack | 1.1 | Inhibit Response Function |  | None | Application Log: Application Log Content, Network Traffic: Network Traffic Content, Network Traffic: Network Traffic Flow, Operational Databases: Process History/Live Data |  | (Citation: Anton Cherepanov, ESET June 2017),(Citation: WPXI Aliquippa Water November 2023),(Citation: Claroty Fuxnet 2024),(Citation: Spenneberg, Ralf, Maik Brggemann, and Hendrik Schwartke March 2016),(Citation: Jamie Tarabay and Katrina Manson December 2023),(Citation: Ukraine15 - EISAC - 201603),(Citation: Frank Bajak and Marc Levy December 2023),(Citation: ICS-CERT August 2018),(Citation: CISA Unitronics November 2023),(Citation: CISA AA23-335A IRGC-Affiliated December 2023),,
T0815 | attack-pattern--56ddc820-6cfb-407f-850b-52c035d123ac | Denial of View | Adversaries may cause a denial of view in attempt to disrupt and prevent operator oversight on the status of an ICS environment. This may manifest itself as a temporary communication failure between a device and its control source, where the interface recovers and becomes available once the interference ceases. (Citation: Corero) (Citation: Michael J. Assante and Robert M. Lee) (Citation: Tyson Macaulay) An adversary may attempt to deny operator visibility by preventing them from receiving status and reporting messages. Denying this view may temporarily block and prevent operators from noticing a change in state or anomalous behavior. The environment's data and processes may still be operational, but functioning in an unintended or adversarial manner. | https://attack.mitre.org/techniques/T0815 | 21 May 2020 | 13 October 2023 | ics-attack | 1.1 | Impact |  | None |  |  | (Citation: Anton Cherepanov, ESET June 2017),(Citation: Marshall Abrams July 2008),(Citation: Department of Homeland Security October 2009),(Citation: National Institute of Standards and Technology April 2013),(Citation: M. Rentschler and H. Heine),
T0868 | attack-pattern--2aa406ed-81c3-4c1d-ba83-cfbee5a2847a | Detect Operating Mode | Adversaries may gather information about a PLCs or controllers current operating mode. Operating modes dictate what change or maintenance functions can be manipulated and are often controlled by a key switch on the PLC (e.g., run, prog [program], and remote). Knowledge of these states may be valuable to an adversary to determine if they are able to reprogram the PLC. Operating modes and the mechanisms by which they are selected often vary by vendor and product line. Some commonly implemented operating modes are described below: * Program - This mode must be enabled before changes can be made to a devices program. This allows program uploads and downloads between the device and an engineering workstation. Often the PLCs logic Is halted, and all outputs may be forced off. (Citation: N.A. October 2017) * Run - Execution of the devices program occurs in this mode. Input and output (values, points, tags, elements, etc.) are monitored and used according to the programs logic.[Program Upload](https://attack.mitre.org/techniques/T0845) and [Program Download](https://attack.mitre.org/techniques/T0843) are disabled while in this mode. (Citation: Omron) (Citation: Machine Information Systems 2007) (Citation: N.A. October 2017) (Citation: PLCgurus 2021) * Remote - Allows for remote changes to a PLCs operation mode. (Citation: PLCgurus 2021) * Stop - The PLC and program is stopped, while in this mode, outputs are forced off. (Citation: Machine Information Systems 2007) * Reset - Conditions on the PLC are reset to their original states. Warm resets may retain some memory while cold resets will reset all I/O and data registers. (Citation: Machine Information Systems 2007) * Test / Monitor mode - Similar to run mode, I/O is processed, although this mode allows for monitoring, force set, resets, and more generally tuning or debugging of the system. Often monitor mode may be used as a trial for initialization. (Citation: Omron) | https://attack.mitre.org/techniques/T0868 | 21 May 2020 | 13 October 2023 | ics-attack | 1.0 | Collection |  | None | Network Traffic: Network Traffic Content |  | (Citation: MDudek-ICS),(Citation: Department of Homeland Security September 2016),
T0816 | attack-pattern--25dfc8ad-bd73-4dfd-84a9-3c3d383f76e9 | Device Restart/Shutdown | Adversaries may forcibly restart or shutdown a device in an ICS environment to disrupt and potentially negatively impact physical processes. Methods of device restart and shutdown exist in some devices as built-in, standard functionalities. These functionalities can be executed using interactive device web interfaces, CLIs, and network protocol commands. Unexpected restart or shutdown of control system devices may prevent expected response functions happening during critical states. A device restart can also be a sign of malicious device modifications, as many updates require a shutdown in order to take effect. | https://attack.mitre.org/techniques/T0816 | 21 May 2020 | 13 October 2023 | ics-attack | 1.1 | Inhibit Response Function |  | None | Application Log: Application Log Content, Network Traffic: Network Traffic Content, Network Traffic: Network Traffic Flow, Operational Databases: Device Alarm |  | (Citation: Anton Cherepanov, ESET June 2017),(Citation: Ukraine15 - EISAC - 201603),(Citation: Booz Allen Hamilton),(Citation: Department of Homeland Security September 2016),
T0817 | attack-pattern--7830cfcf-b268-4ac0-a69e-73c6affbae9a | Drive-by Compromise | Adversaries may gain access to a system during a drive-by compromise, when a user visits a website as part of a regular browsing session. With this technique, the user's web browser is targeted and exploited simply by visiting the compromised website. The adversary may target a specific community, such as trusted third party suppliers or other industry specific groups, which often visit the target website. This kind of targeted attack relies on a common interest, and is known as a strategic web compromise or watering hole attack. The National Cyber Awareness System (NCAS) has issued a Technical Alert (TA) regarding Russian government cyber activity targeting critical infrastructure sectors. (Citation: Cybersecurity & Infrastructure Security Agency March 2018) Analysis by DHS and FBI has noted two distinct categories of victims in the Dragonfly campaign on the Western energy sector: staging and intended targets. The adversary targeted the less secure networks of staging targets, including trusted third-party suppliers and related peripheral organizations. Initial access to the intended targets used watering hole attacks to target process control, ICS, and critical infrastructure related trade publications and informational websites. | https://attack.mitre.org/techniques/T0817 | 21 May 2020 | 13 October 2023 | ics-attack | 1.0 | Initial Access |  | None | Application Log: Application Log Content, File: File Creation, Network Traffic: Network Connection Creation, Network Traffic: Network Traffic Content, Process: Process Creation |  | (Citation: Chris Bing May 2018),(Citation: Orkhan Mamedov, Fedor Sinitsyn, Anton Ivanov October 2017),(Citation: Eduard Kovacs May 2018),(Citation: Symantec Security Response July 2014),,
T0871 | attack-pattern--5a2610f6-9fff-41e1-bc27-575ca20383d4 | Execution through API | Adversaries may attempt to leverage Application Program Interfaces (APIs) used for communication between control software and the hardware. Specific functionality is often coded into APIs which can be called by software to engage specific functions on a device or other software. | https://attack.mitre.org/techniques/T0871 | 21 May 2020 | 13 October 2023 | ics-attack | 1.1 | Execution |  | None | Process: OS API Execution |  | (Citation: Jos Wetzels January 2018),(Citation: MITRE June 2020),(Citation: McCarthy, J et al. July 2018),
T0819 | attack-pattern--32632a95-6856-47b9-9ab7-fea5cd7dce00 | Exploit Public-Facing Application | Adversaries may leverage weaknesses to exploit internet-facing software for initial access into an industrial network. Internet-facing software may be user applications, underlying networking implementations, an assets operating system, weak defenses, etc. Targets of this technique may be intentionally exposed for the purpose of remote management and visibility. An adversary may seek to target public-facing applications as they may provide direct access into an ICS environment or the ability to move into the ICS network. Publicly exposed applications may be found through online tools that scan the internet for open ports and services. Version numbers for the exposed application may provide adversaries an ability to target specific known vulnerabilities. Exposed control protocol or remote access ports found in Commonly Used Port may be of interest by adversaries. | https://attack.mitre.org/techniques/T0819 | 21 May 2020 | 13 October 2023 | ics-attack | 1.0 | Initial Access |  | None | Application Log: Application Log Content, Network Traffic: Network Traffic Content |  | (Citation: ICS CERT September 2018),(Citation: ICS-CERT December 2014),(Citation: Karen Scarfone; Paul Hoffman September 2009),(Citation: National Institute of Standards and Technology April 2013),(Citation: Keith Stouffer May 2015),
T0820 | attack-pattern--9f947a1c-3860-48a8-8af0-a2dfa3efde03 | Exploitation for Evasion | Adversaries may exploit a software vulnerability to take advantage of a programming error in a program, service, or within the operating system software or kernel itself to evade detection. Vulnerabilities may exist in software that can be used to disable or circumvent security features. Adversaries may have prior knowledge through [Remote System Information Discovery](https://attack.mitre.org/techniques/T0888) about security features implemented on control devices. These device security features will likely be targeted directly for exploitation. There are examples of firmware RAM/ROM consistency checks on control devices being targeted by adversaries to enable the installation of malicious [System Firmware](https://attack.mitre.org/techniques/T0857). | https://attack.mitre.org/techniques/T0820 | 21 May 2020 | 13 October 2023 | ics-attack | 1.1 | Evasion |  | None | Application Log: Application Log Content |  | (Citation: DHS CISA February 2019),(Citation: ICS-CERT December 2018),(Citation: Schneider Electric January 2018),(Citation: The Office of Nuclear Reactor Regulation),(Citation: Microsoft Security Response Center August 2017),(Citation: Dan Goodin March 2017),(Citation: Wikipedia),
T0890 | attack-pattern--cfe68e93-ce94-4c0f-a57d-3aa72cedd618 | Exploitation for Privilege Escalation | Adversaries may exploit software vulnerabilities in an attempt to elevate privileges. Exploitation of a software vulnerability occurs when an adversary takes advantage of a programming error in a program, service, or within the operating system software or kernel itself to execute adversary-controlled code. Security constructs such as permission levels will often hinder access to information and use of certain techniques, so adversaries will likely need to perform privilege escalation to include use of software exploitation to circumvent those restrictions. (Citation: The MITRE Corporation) When initially gaining access to a system, an adversary may be operating within a lower privileged process which will prevent them from accessing certain resources on the system. Vulnerabilities may exist, usually in operating system components and software commonly running at higher permissions, that can be exploited to gain higher levels of access on the system. This could enable someone to move from unprivileged or user level permissions to SYSTEM or root permissions depending on the component that is vulnerable. This may be a necessary step for an adversary compromising an endpoint system that has been properly configured and limits other privilege escalation methods. (Citation: The MITRE Corporation) | https://attack.mitre.org/techniques/T0890 | 13 April 2021 | 13 October 2023 | ics-attack | 1.1 | Privilege Escalation |  | None | Application Log: Application Log Content |  | (Citation: DHS CISA February 2019),(Citation: Wylie-22),(Citation: Microsoft Security Response Center August 2017),(Citation: Dan Goodin March 2017),(Citation: Wikipedia),
T0866 | attack-pattern--85a45294-08f1-4539-bf00-7da08aa7b0ee | Exploitation of Remote Services | Adversaries may exploit a software vulnerability to take advantage of a programming error in a program, service, or within the operating system software or kernel itself to enable remote service abuse. A common goal for post-compromise exploitation of remote services is for initial access into and lateral movement throughout the ICS environment to enable access to targeted systems. (Citation: Enterprise ATT&CK) ICS asset owners and operators have been affected by ransomware (or disruptive malware masquerading as ransomware) migrating from enterprise IT to ICS environments: WannaCry, NotPetya, and BadRabbit. In each of these cases, self-propagating (wormable) malware initially infected IT networks, but through exploit (particularly the SMBv1-targeting MS17-010 vulnerability) spread to industrial networks, producing significant impacts. (Citation: Joe Slowik April 2019) | https://attack.mitre.org/techniques/T0866 | 21 May 2020 | 13 October 2023 | ics-attack | 1.0 | Initial Access, Lateral Movement |  | None | Application Log: Application Log Content, Network Traffic: Network Traffic Content |  | (Citation: Joe Slowik April 2019),(Citation: Nicolas Falliere, Liam O Murchu, Eric Chien February 2011),(Citation: Microsoft Security Response Center August 2017),(Citation: Dan Goodin March 2017),(Citation: Keith Stouffer May 2015),(Citation: Wikipedia),
T0822 | attack-pattern--8d2f3bab-507c-4424-b58b-edc977bd215c | External Remote Services | Adversaries may leverage external remote services as a point of initial access into your network. These services allow users to connect to internal network resources from external locations. Examples are VPNs, Citrix, and other access mechanisms. Remote service gateways often manage connections and credential authentication for these services. (Citation: Daniel Oakley, Travis Smith, Tripwire) External remote services allow administration of a control system from outside the system. Often, vendors and internal engineering groups have access to external remote services to control system networks via the corporate network. In some cases, this access is enabled directly from the internet. While remote access enables ease of maintenance when a control system is in a remote area, compromise of remote access solutions is a liability. The adversary may use these services to gain access to and execute attacks against a control system network. Access to valid accounts is often a requirement. As they look for an entry point into the control system network, adversaries may begin searching for existing point-to-point VPN implementations at trusted third party networks or through remote support employee connections where split tunneling is enabled. (Citation: Electricity Information Sharing and Analysis Center; SANS Industrial Control Systems March 2016) | https://attack.mitre.org/techniques/T0822 | 21 May 2020 | 13 October 2023 | ics-attack | 1.1 | Initial Access |  | None | Application Log: Application Log Content, Logon Session: Logon Session Metadata, Network Traffic: Network Traffic Flow |  | (Citation: Claroty Fuxnet 2024),(Citation: Marshall Abrams July 2008),(Citation: Booz Allen Hamilton),(Citation: Department of Homeland Security September 2016),(Citation: Keith Stouffer May 2015),
T0823 | attack-pattern--b0628bfc-5376-4a38-9182-f324501cb4cf | Graphical User Interface | Adversaries may attempt to gain access to a machine via a Graphical User Interface (GUI) to enhance execution capabilities. Access to a GUI allows a user to interact with a computer in a more visual manner than a CLI. A GUI allows users to move a cursor and click on interface objects, with a mouse and keyboard as the main input devices, as opposed to just using the keyboard. If physical access is not an option, then access might be possible via protocols such as VNC on Linux-based and Unix-based operating systems, and RDP on Windows operating systems. An adversary can use this access to execute programs and applications on the target machine. | https://attack.mitre.org/techniques/T0823 | 21 May 2020 | 13 October 2023 | ics-attack | 1.1 | Execution |  | None | Command: Command Execution, Logon Session: Logon Session Creation, Module: Module Load, Process: Process Creation |  | (Citation: Ukraine15 - EISAC - 201603),,
T0891 | attack-pattern--c9a8d958-fcdb-40d2-af4c-461c8031651a | Hardcoded Credentials | Adversaries may leverage credentials that are hardcoded in software or firmware to gain an unauthorized interactive user session to an asset. Examples credentials that may be hardcoded in an asset include: * Username/Passwords * Cryptographic keys/Certificates * API tokens Unlike [Default Credentials](https://attack.mitre.org/techniques/T0812), these credentials are built into the system in a way that they either cannot be changed by the asset owner, or may be infeasible to change because of the impact it would cause to the control system operation. These credentials may be reused across whole product lines or device models and are often not published or known to the owner and operators of the asset. Adversaries may utilize these hardcoded credentials to move throughout the control system environment or provide reliable access for their tools to interact with industrial assets. | https://attack.mitre.org/techniques/T0891 | 29 September 2022 | 13 October 2023 | ics-attack | 1.0 | Lateral Movement, Persistence |  | None | Logon Session: Logon Session Creation, Network Traffic: Network Traffic Content | Aagam Shah, @neutrinoguy, ABB | (Citation: Nicolas Falliere, Liam O Murchu, Eric Chien February 2011),(Citation: Wylie-22),,
T0874 | attack-pattern--ab390887-afc0-4715-826d-b1b167d522ae | Hooking | Adversaries may hook into application programming interface (API) functions used by processes to redirect calls for execution and privilege escalation means. Windows processes often leverage these API functions to perform tasks that require reusable system resources. Windows API functions are typically stored in dynamic-link libraries (DLLs) as exported functions. (Citation: Enterprise ATT&CK) One type of hooking seen in ICS involves redirecting calls to these functions via import address table (IAT) hooking. IAT hooking uses modifications to a process IAT, where pointers to imported API functions are stored. (Citation: Nicolas Falliere, Liam O Murchu, Eric Chien February 2011) | https://attack.mitre.org/techniques/T0874 | 21 May 2020 | 13 October 2023 | ics-attack | 1.2 | Execution, Privilege Escalation |  | None | Process: OS API Execution, Process: Process Metadata |  | (Citation: Nicolas Falliere, Liam O Murchu, Eric Chien February 2011),(Citation: Jos Wetzels January 2018),,
T0877 | attack-pattern--53a48c74-0025-45f4-b04a-baa853df8204 | I/O Image | Adversaries may seek to capture process values related to the inputs and outputs of a PLC. During the scan cycle, a PLC reads the status of all inputs and stores them in an image table. (Citation: Nanjundaiah, Vaidyanath) The image table is the PLCs internal storage location where values of inputs/outputs for one scan are stored while it executes the user program. After the PLC has solved the entire logic program, it updates the output image table. The contents of this output image table are written to the corresponding output points in I/O Modules. The Input and Output Image tables described above make up the I/O Image on a PLC. This image is used by the user program instead of directly interacting with physical I/O. (Citation: Spenneberg, Ralf 2016) Adversaries may collect the I/O Image state of a PLC by utilizing a devices [Native API](https://attack.mitre.org/techniques/T0834) to access the memory regions directly. The collection of the PLCs I/O state could be used to replace values or inform future stages of an attack. | https://attack.mitre.org/techniques/T0877 | 21 May 2020 | 13 October 2023 | ics-attack | 1.1 | Collection |  | None | Asset: Software |  | (Citation: Nicolas Falliere, Liam O Murchu, Eric Chien February 2011),,
T0872 | attack-pattern--53a26eee-1080-4d17-9762-2027d5a1b805 | Indicator Removal on Host | Adversaries may attempt to remove indicators of their presence on a system in an effort to cover their tracks. In cases where an adversary may feel detection is imminent, they may try to overwrite, delete, or cover up changes they have made to the device. | https://attack.mitre.org/techniques/T0872 | 21 May 2020 | 13 October 2023 | ics-attack | 1.0 | Evasion |  | None | Command: Command Execution, File: File Deletion, File: File Metadata, File: File Modification, Process: OS API Execution, Process: Process Creation, Windows Registry: Windows Registry Key Deletion, Windows Registry: Windows Registry Key Modification |  | (Citation: FireEye TRITON Dec 2017),(Citation: Anton Cherepanov),(Citation: Jos Wetzels January 2018),(Citation: National Institute of Standards and Technology April 2013),(Citation: Keith Stouffer May 2015),
T0883 | attack-pattern--f8df6b57-14bc-425f-9a91-6f59f6799307 | Internet Accessible Device | Adversaries may gain access into industrial environments through systems exposed directly to the internet for remote access rather than through [External Remote Services](https://attack.mitre.org/techniques/T0822). Internet Accessible Devices are exposed to the internet unintentionally or intentionally without adequate protections. This may allow for adversaries to move directly into the control system network. Access onto these devices is accomplished without the use of exploits, these would be represented within the [Exploit Public-Facing Application](https://attack.mitre.org/techniques/T0819) technique. Adversaries may leverage built in functions for remote access which may not be protected or utilize minimal legacy protections that may be targeted. (Citation: NCCIC January 2014) These services may be discoverable through the use of online scanning tools. In the case of the Bowman dam incident, adversaries leveraged access to the dam control network through a cellular modem. Access to the device was protected by password authentication, although the application was vulnerable to brute forcing. (Citation: NCCIC January 2014) (Citation: Danny Yadron December 2015) (Citation: Mark Thompson March 2016) In Trend Micros manufacturing deception operations adversaries were detected leveraging direct internet access to an ICS environment through the exposure of operational protocols such as Siemens S7, Omron FINS, and EtherNet/IP, in addition to misconfigured VNC access. (Citation: Stephen Hilt, Federico Maggi, Charles Perine, Lord Remorin, Martin Rsler, and Rainer Vosseler) | https://attack.mitre.org/techniques/T0883 | 21 May 2020 | 13 October 2023 | ics-attack | 1.0 | Initial Access |  | None | Logon Session: Logon Session Metadata, Network Traffic: Network Traffic Content, Network Traffic: Network Traffic Flow |  | (Citation: Lisa Zahner December 2023),(Citation: CISA AA23-335A IRGC-Affiliated December 2023),(Citation: Claroty Fuxnet 2024),,
T0867 | attack-pattern--ead7bd34-186e-4c79-9a4d-b65bcce6ed9d | Lateral Tool Transfer | Adversaries may transfer tools or other files from one system to another to stage adversary tools or other files over the course of an operation. (Citation: Enterprise ATT&CK) Copying of files may also be performed laterally between internal victim systems to support Lateral Movement with remote Execution using inherent file sharing protocols such as file sharing over SMB to connected network shares. (Citation: Enterprise ATT&CK) In control systems environments, malware may use SMB and other file sharing protocols to move laterally through industrial networks. | https://attack.mitre.org/techniques/T0867 | 21 May 2020 | 13 October 2023 | ics-attack | 1.1 | Lateral Movement |  | None | Command: Command Execution, File: File Creation, File: File Metadata, Network Share: Network Share Access, Network Traffic: Network Traffic Content, Network Traffic: Network Traffic Flow, Process: Process Creation |  | (Citation: Nicolas Falliere, Liam O Murchu, Eric Chien February 2011),(Citation: CISA-AA22-103A),(Citation: Booz Allen Hamilton),(Citation: Wylie-22),(Citation: Joe Slowik April 2019),(Citation: Dragos Crashoverride 2018),(Citation: FireEye TEMP.Veles 2018),(Citation: Gardiner, J., Cova, M., Nagaraja, S February 2014),
T0826 | attack-pattern--b5b9bacb-97f2-4249-b804-47fd44de1f95 | Loss of Availability | Adversaries may attempt to disrupt essential components or systems to prevent owner and operator from delivering products or services. (Citation: Corero) (Citation: Michael J. Assante and Robert M. Lee) (Citation: Tyson Macaulay) Adversaries may leverage malware to delete or encrypt critical data on HMIs, workstations, or databases. In the 2021 Colonial Pipeline ransomware incident, pipeline operations were temporally halted on May 7th and were not fully restarted until May 12th. (Citation: Colonial Pipeline Company May 2021) | https://attack.mitre.org/techniques/T0826 | 21 May 2020 | 13 October 2023 | ics-attack | 1.0 | Impact |  | None |  |  | (Citation: Catalin Cimpanu April 2016),(Citation: Jamie Tarabay and Katrina Manson December 2023),(Citation: Ukraine15 - EISAC - 201603),(Citation: Booz Allen Hamilton),(Citation: Department of Homeland Security October 2009),(Citation: National Institute of Standards and Technology April 2013),(Citation: M. Rentschler and H. Heine),
T0827 | attack-pattern--a81696ef-c106-482c-8f80-59c30f2569fb | Loss of Control | Adversaries may seek to achieve a sustained loss of control or a runaway condition in which operators cannot issue any commands even if the malicious interference has subsided. (Citation: Corero) (Citation: Michael J. Assante and Robert M. Lee) (Citation: Tyson Macaulay) The German Federal Office for Information Security (BSI) reported a targeted attack on a steel mill in its 2014 IT Security Report.(Citation: BSI State of IT Security 2014) These targeted attacks affected industrial operations and resulted in breakdowns of control system components and even entire installations. As a result of these breakdowns, massive impact resulted in damage and unsafe conditions from the uncontrolled shutdown of a blast furnace. | https://attack.mitre.org/techniques/T0827 | 21 May 2020 | 13 October 2023 | ics-attack | 1.0 | Impact |  | None |  | Dragos Threat Intelligence | (Citation: Anton Cherepanov, ESET June 2017),(Citation: Kevin Beaumont),(Citation: Ukraine15 - EISAC - 201603),(Citation: Hydro),(Citation: Department of Homeland Security October 2009),(Citation: National Institute of Standards and Technology April 2013),(Citation: M. Rentschler and H. Heine),
T0828 | attack-pattern--63b6942d-8359-4506-bfb3-cf87aa8120ee | Loss of Productivity and Revenue | Adversaries may cause loss of productivity and revenue through disruption and even damage to the availability and integrity of control system operations, devices, and related processes. This technique may manifest as a direct effect of an ICS-targeting attack or tangentially, due to an IT-targeting attack against non-segregated environments. In cases where these operations or services are brought to a halt, the loss of productivity may eventually present an impact for the end-users or consumers of products and services. The disrupted supply-chain may result in supply shortages and increased prices, among other consequences. A ransomware attack on an Australian beverage company resulted in the shutdown of some manufacturing sites, including precautionary halts to protect key systems. (Citation: Paganini, Pierluigi June 2020) The company announced the potential for temporary shortages of their products following the attack. (Citation: Paganini, Pierluigi June 2020) (Citation: Lion Corporation June 2020) In the 2021 Colonial Pipeline ransomware incident, the pipeline was unable to transport approximately 2.5 million barrels of fuel per day to the East Coast. (Citation: Colonial Pipeline Company May 2021) | https://attack.mitre.org/techniques/T0828 | 21 May 2020 | 13 October 2023 | ics-attack | 1.0 | Impact |  | None |  |  | (Citation: Kevin Beaumont),(Citation: Kelly Jackson Higgins),(Citation: David Voreacos, Katherine Chinglinsky, Riley Griffin December 2019),(Citation: Booz Allen Hamilton),(Citation: Hydro),(Citation: Marc-Etienne M.Lveill October 2017),(Citation: FireEye TRITON Dec 2017),(Citation: Davey Winder June 2020),(Citation: Selena Larson, Camille Singleton December 2020),(Citation: Catalin Cimpanu April 2016),(Citation: Jamie Tarabay and Katrina Manson December 2023),(Citation: Ukraine15 - EISAC - 201603),(Citation: Department of Homeland Security October 2009),
T0837 | attack-pattern--2bb4d762-bf4a-4bc3-9318-15cc6a354163 | Loss of Protection | Adversaries may compromise protective system functions designed to prevent the effects of faults and abnormal conditions. This can result in equipment damage, prolonged process disruptions and hazards to personnel. Many faults and abnormal conditions in process control happen too quickly for a human operator to react to. Speed is critical in correcting these conditions to limit serious impacts such as Loss of Control and Property Damage. Adversaries may target and disable protective system functions as a prerequisite to subsequent attack execution or to allow for future faults and abnormal conditions to go unchecked. Detection of a Loss of Protection by operators can result in the shutdown of a process due to strict policies regarding protection systems. This can cause a Loss of Productivity and Revenue and may meet the technical goals of adversaries seeking to cause process disruptions. | https://attack.mitre.org/techniques/T0837 | 12 April 2021 | 13 October 2023 | ics-attack | 1.0 | Impact |  | None |  |  | (Citation: Joe Slowik August 2019),,
T0880 | attack-pattern--5fa00fdd-4a55-4191-94a0-564181d7fec2 | Loss of Safety | Adversaries may compromise safety system functions designed to maintain safe operation of a process when unacceptable or dangerous conditions occur. Safety systems are often composed of the same elements as control systems but have the sole purpose of ensuring the process fails in a predetermined safe manner. Many unsafe conditions in process control happen too quickly for a human operator to react to. Speed is critical in correcting these conditions to limit serious impacts such as Loss of Control and Property Damage. Adversaries may target and disable safety system functions as a prerequisite to subsequent attack execution or to allow for future unsafe conditionals to go unchecked. Detection of a Loss of Safety by operators can result in the shutdown of a process due to strict policies regarding safety systems. This can cause a Loss of Productivity and Revenue and may meet the technical goals of adversaries seeking to cause process disruptions. | https://attack.mitre.org/techniques/T0880 | 21 May 2020 | 13 October 2023 | ics-attack | 1.0 | Impact |  | None |  |  | (Citation: Blake Johnson, Dan Caban, Marina Krotofil, Dan Scali, Nathan Brubaker, Christopher Glyer December 2017),(Citation: A G Foord, W G Gulland, C R Howard, T Kellacher, W H Smith 2004),
T0829 | attack-pattern--138979ba-0430-4de6-a128-2fc0b056ba36 | Loss of View | Adversaries may cause a sustained or permanent loss of view where the ICS equipment will require local, hands-on operator intervention; for instance, a restart or manual operation. By causing a sustained reporting or visibility loss, the adversary can effectively hide the present state of operations. This loss of view can occur without affecting the physical processes themselves. (Citation: Corero) (Citation: Michael J. Assante and Robert M. Lee) (Citation: Tyson Macaulay) | https://attack.mitre.org/techniques/T0829 | 21 May 2020 | 13 October 2023 | ics-attack | 1.0 | Impact |  | None |  |  | (Citation: Anton Cherepanov, ESET June 2017),(Citation: Kevin Beaumont),(Citation: Booz Allen Hamilton),(Citation: Hydro),(Citation: Claroty Fuxnet 2024),(Citation: Jamie Tarabay and Katrina Manson December 2023),(Citation: CISA AA23-335A IRGC-Affiliated December 2023),(Citation: Department of Homeland Security October 2009),(Citation: National Institute of Standards and Technology April 2013),(Citation: M. Rentschler and H. Heine),
T0835 | attack-pattern--36e9f5bc-ac13-4da4-a2f4-01f4877d9004 | Manipulate I/O Image | Adversaries may manipulate the I/O image of PLCs through various means to prevent them from functioning as expected. Methods of I/O image manipulation may include overriding the I/O table via direct memory manipulation or using the override function used for testing PLC programs. (Citation: Dr. Kelvin T. Erickson December 2010) During the scan cycle, a PLC reads the status of all inputs and stores them in an image table. (Citation: Nanjundaiah, Vaidyanath) The image table is the PLCs internal storage location where values of inputs/outputs for one scan are stored while it executes the user program. After the PLC has solved the entire logic program, it updates the output image table. The contents of this output image table are written to the corresponding output points in I/O Modules. One of the unique characteristics of PLCs is their ability to override the status of a physical discrete input or to override the logic driving a physical output coil and force the output to a desired status. | https://attack.mitre.org/techniques/T0835 | 21 May 2020 | 13 October 2023 | ics-attack | 1.1 | Inhibit Response Function |  | None | Asset: Software |  | (Citation: Spenneberg, Ralf, Maik Brggemann, and Hendrik Schwartke March 2016),(Citation: Nicolas Falliere, Liam O Murchu, Eric Chien February 2011),,
T0831 | attack-pattern--1af9e3fd-2bcc-414d-adbd-fe3b95c02ca1 | Manipulation of Control | Adversaries may manipulate physical process control within the industrial environment. Methods of manipulating control can include changes to set point values, tags, or other parameters. Adversaries may manipulate control systems devices or possibly leverage their own, to communicate with and command physical control processes. The duration of manipulation may be temporary or longer sustained, depending on operator detection. Methods of Manipulation of Control include: * Man-in-the-middle * Spoof command message * Changing setpoints A Polish student used a remote controller device to interface with the Lodz city tram system in Poland. (Citation: John Bill May 2017) (Citation: Shelley Smith February 2008) (Citation: Bruce Schneier January 2008) Using this remote, the student was able to capture and replay legitimate tram signals. As a consequence, four trams were derailed and twelve people injured due to resulting emergency stops. (Citation: Shelley Smith February 2008) The track controlling commands issued may have also resulted in tram collisions, a further risk to those on board and nearby the areas of impact. (Citation: Bruce Schneier January 2008) | https://attack.mitre.org/techniques/T0831 | 21 May 2020 | 13 October 2023 | ics-attack | 1.0 | Impact |  | None |  |  | (Citation: Anton Cherepanov, ESET June 2017),(Citation: Nicolas Falliere, Liam O Murchu, Eric Chien February 2011),(Citation: Ukraine15 - EISAC - 201603),(Citation: Department of Homeland Security October 2009),
T0832 | attack-pattern--4c2e1408-9d68-4187-8e6b-a77bc52700ec | Manipulation of View | Adversaries may attempt to manipulate the information reported back to operators or controllers. This manipulation may be short term or sustained. During this time the process itself could be in a much different state than what is reported. (Citation: Corero) (Citation: Michael J. Assante and Robert M. Lee) (Citation: Tyson Macaulay) Operators may be fooled into doing something that is harmful to the system in a loss of view situation. With a manipulated view into the systems, operators may issue inappropriate control sequences that introduce faults or catastrophic failures into the system. Business analysis systems can also be provided with inaccurate data leading to bad management decisions. | https://attack.mitre.org/techniques/T0832 | 21 May 2020 | 13 October 2023 | ics-attack | 1.0 | Impact |  | None |  |  | (Citation: Anton Cherepanov, ESET June 2017),(Citation: Nicolas Falliere, Liam O Murchu, Eric Chien February 2011),(Citation: Langer Stuxnet),(Citation: Department of Homeland Security October 2009),
T0849 | attack-pattern--ba203963-3182-41ac-af14-7e7ebc83cd61 | Masquerading | Adversaries may use masquerading to disguise a malicious application or executable as another file, to avoid operator and engineer suspicion. Possible disguises of these masquerading files can include commonly found programs, expected vendor executables and configuration files, and other commonplace application and naming conventions. By impersonating expected and vendor-relevant files and applications, operators and engineers may not notice the presence of the underlying malicious content and possibly end up running those masquerading as legitimate functions. Applications and other files commonly found on Windows systems or in engineering workstations have been impersonated before. This can be as simple as renaming a file to effectively disguise it in the ICS environment. | https://attack.mitre.org/techniques/T0849 | 21 May 2020 | 13 October 2023 | ics-attack | 1.1 | Evasion |  | None | Command: Command Execution, File: File Metadata, File: File Modification, Process: Process Metadata, Scheduled Job: Scheduled Job Creation, Scheduled Job: Scheduled Job Modification, Service: Service Creation, Service: Service Modification |  | (Citation: Dragos Threat Intelligence February 2020),(Citation: Nicolas Falliere, Liam O Murchu, Eric Chien February 2011),(Citation: Tom Fakterman August 2019),(Citation: DHS CISA February 2019),(Citation: FireEye TRITON),(Citation: Dragos Crashoverride 2018),,
T0838 | attack-pattern--e5de767e-f513-41cd-aa15-33f6ce5fbf92 | Modify Alarm Settings | Adversaries may modify alarm settings to prevent alerts that may inform operators of their presence or to prevent responses to dangerous and unintended scenarios. Reporting messages are a standard part of data acquisition in control systems. Reporting messages are used as a way to transmit system state information and acknowledgements that specific actions have occurred. These messages provide vital information for the management of a physical process, and keep operators, engineers, and administrators aware of the state of system devices and physical processes. If an adversary is able to change the reporting settings, certain events could be prevented from being reported. This type of modification can also prevent operators or devices from performing actions to keep the system in a safe state. If critical reporting messages cannot trigger these actions then a [Impact](https://attack.mitre.org/tactics/TA0105) could occur. In ICS environments, the adversary may have to use [Alarm Suppression](https://attack.mitre.org/techniques/T0878) or contend with multiple alarms and/or alarm propagation to achieve a specific goal to evade detection or prevent intended responses from occurring. (Citation: Jos Wetzels, Marina Krotofil 2019) Methods of suppression often rely on modification of alarm settings, such as modifying in memory code to fixed values or tampering with assembly level instruction code. | https://attack.mitre.org/techniques/T0838 | 21 May 2020 | 13 October 2023 | ics-attack | 1.2 | Inhibit Response Function |  | None | Application Log: Application Log Content, Asset: Asset Inventory, Network Traffic: Network Traffic Content, Operational Databases: Process History/Live Data |  | (Citation: Marshall Abrams July 2008),(Citation: Department of Homeland Security September 2016),(Citation: N/A),
T0821 | attack-pattern--09a61657-46e1-439e-b3ed-3e4556a78243 | Modify Controller Tasking | Adversaries may modify the tasking of a controller to allow for the execution of their own programs. This can allow an adversary to manipulate the execution flow and behavior of a controller. According to 61131-3, the association of a Task with a Program Organization Unit (POU) defines a task association. (Citation: IEC February 2013) An adversary may modify these associations or create new ones to manipulate the execution flow of a controller. Modification of controller tasking can be accomplished using a Program Download in addition to other types of program modification such as online edit and program append. Tasks have properties, such as interval, frequency and priority to meet the requirements of program execution. Some controller vendors implement tasks with implicit, pre-defined properties whereas others allow for these properties to be formulated explicitly. An adversary may associate their program with tasks that have a higher priority or execute associated programs more frequently. For instance, to ensure cyclic execution of their program on a Siemens controller, an adversary may add their program to the task, Organization Block 1 (OB1). | https://attack.mitre.org/techniques/T0821 | 13 April 2021 | 13 October 2023 | ics-attack | 1.2 | Execution |  | None | Application Log: Application Log Content, Asset: Software, Operational Databases: Device Alarm |  | (Citation: DHS CISA February 2019),(Citation: Spenneberg, Ralf, Maik Brggemann, and Hendrik Schwartke March 2016),(Citation: Nicolas Falliere, Liam O Murchu, Eric Chien February 2011),(Citation: Jos Wetzels January 2018),(Citation: IEC February 2019),
T0836 | attack-pattern--097924ce-a9a9-4039-8591-e0deedfb8722 | Modify Parameter | Adversaries may modify parameters used to instruct industrial control system devices. These devices operate via programs that dictate how and when to perform actions based on such parameters. Such parameters can determine the extent to which an action is performed and may specify additional options. For example, a program on a control system device dictating motor processes may take a parameter defining the total number of seconds to run that motor. An adversary can potentially modify these parameters to produce an outcome outside of what was intended by the operators. By modifying system and process critical parameters, the adversary may cause [Impact](https://attack.mitre.org/tactics/TA0105) to equipment and/or control processes. Modified parameters may be turned into dangerous, out-of-bounds, or unexpected values from typical operations. For example, specifying that a process run for more or less time than it should, or dictating an unusually high, low, or invalid value as a parameter. | https://attack.mitre.org/techniques/T0836 | 21 May 2020 | 13 October 2023 | ics-attack | 1.3 | Impair Process Control |  | None | Application Log: Application Log Content, Asset: Asset Inventory, Network Traffic: Network Traffic Content, Operational Databases: Device Alarm |  | (Citation: Nicolas Falliere, Liam O Murchu, Eric Chien February 2011),(Citation: Marshall Abrams July 2008),(Citation: Industroyer2 Mandiant April 2022),(Citation: Industroyer2 Forescout July 2022),(Citation: Wylie-22),(Citation: PLCTop20 Mar 2023),
T0889 | attack-pattern--fc5fda7e-6b2c-4457-b036-759896a2efa2 | Modify Program | Adversaries may modify or add a program on a controller to affect how it interacts with the physical process, peripheral devices and other hosts on the network. Modification to controller programs can be accomplished using a Program Download in addition to other types of program modification such as online edit and program append. Program modification encompasses the addition and modification of instructions and logic contained in Program Organization Units (POU) (Citation: IEC February 2013) and similar programming elements found on controllers. This can include, for example, adding new functions to a controller, modifying the logic in existing functions and making new calls from one function to another. Some programs may allow an adversary to interact directly with the native API of the controller to take advantage of obscure features or vulnerabilities. | https://attack.mitre.org/techniques/T0889 | 13 April 2021 | 20 October 2023 | ics-attack | 1.2 | Persistence |  | None | Application Log: Application Log Content, Asset: Software, Network Traffic: Network Traffic Content, Operational Databases: Device Alarm |  | (Citation: Spenneberg, Ralf, Maik Brggemann, and Hendrik Schwartke March 2016),(Citation: Nicolas Falliere, Liam O Murchu, Eric Chien February 2011),(Citation: IEC February 2019),
T0839 | attack-pattern--efbf7888-f61b-4572-9c80-7e2965c60707 | Module Firmware | Adversaries may install malicious or vulnerable firmware onto modular hardware devices. Control system devices often contain modular hardware devices. These devices may have their own set of firmware that is separate from the firmware of the main control system equipment. This technique is similar to [System Firmware](https://attack.mitre.org/techniques/T0857), but is conducted on other system components that may not have the same capabilities or level of integrity checking. Although it results in a device re-image, malicious device firmware may provide persistent access to remaining devices. (Citation: Daniel Peck, Dale Peterson January 2009) An easy point of access for an adversary is the Ethernet card, which may have its own CPU, RAM, and operating system. The adversary may attack and likely exploit the computer on an Ethernet card. Exploitation of the Ethernet card computer may enable the adversary to accomplish additional attacks, such as the following: (Citation: Daniel Peck, Dale Peterson January 2009) * Delayed Attack - The adversary may stage an attack in advance and choose when to launch it, such as at a particularly damaging time. * Brick the Ethernet Card - Malicious firmware may be programmed to result in an Ethernet card failure, requiring a factory return. * Random Attack or Failure - The adversary may load malicious firmware onto multiple field devices. Execution of an attack and the time it occurs is generated by a pseudo-random number generator. * A Field Device Worm - The adversary may choose to identify all field devices of the same model, with the end goal of performing a device-wide compromise. * Attack Other Cards on the Field Device - Although it is not the most important module in a field device, the Ethernet card is most accessible to the adversary and malware. Compromise of the Ethernet card may provide a more direct route to compromising other modules, such as the CPU module. | https://attack.mitre.org/techniques/T0839 | 21 May 2020 | 13 October 2023 | ics-attack | 1.1 | Impair Process Control, Persistence |  | None | Application Log: Application Log Content, Firmware: Firmware Modification, Network Traffic: Network Traffic Content, Operational Databases: Device Alarm |  | ,(Citation: Intel),(Citation: Department of Homeland Security September 2016),(Citation: ESET Research Whitepapers September 2018),(Citation: N/A),
T0801 | attack-pattern--2d0d40ad-22fa-4cc8-b264-072557e1364b | Monitor Process State | Adversaries may gather information about the physical process state. This information may be used to gain more information about the process itself or used as a trigger for malicious actions. The sources of process state information may vary such as, OPC tags, historian data, specific PLC block information, or network traffic. | https://attack.mitre.org/techniques/T0801 | 21 May 2020 | 13 October 2023 | ics-attack | 1.0 | Collection |  | None | Application Log: Application Log Content, Network Traffic: Network Traffic Content |  | (Citation: Anton Cherepanov, ESET June 2017),(Citation: Nicolas Falliere, Liam O Murchu, Eric Chien February 2011),(Citation: Industroyer2 Forescout July 2022),,
T0834 | attack-pattern--b52870cc-83f3-473c-b895-72d91751030b | Native API | Adversaries may directly interact with the native OS application programming interface (API) to access system functions. Native APIs provide a controlled means of calling low-level OS services within the kernel, such as those involving hardware/devices, memory, and processes. (Citation: The MITRE Corporation May 2017) These native APIs are leveraged by the OS during system boot (when other system components are not yet initialized) as well as carrying out tasks and requests during routine operations. Functionality provided by native APIs are often also exposed to user-mode applications via interfaces and libraries. For example, functions such as memcpy and direct operations on memory registers can be used to modify user and system memory space. | https://attack.mitre.org/techniques/T0834 | 13 April 2021 | 13 October 2023 | ics-attack | 1.0 | Execution |  | None | Process: OS API Execution |  | (Citation: Spenneberg, Ralf, Maik Brggemann, and Hendrik Schwartke March 2016),(Citation: Nicolas Falliere, Liam O Murchu, Eric Chien February 2011),(Citation: Jos Wetzels January 2018),,
T0840 | attack-pattern--ea0c980c-5cf0-43a7-a049-59c4c207566e | Network Connection Enumeration | Adversaries may perform network connection enumeration to discover information about device communication patterns. If an adversary can inspect the state of a network connection with tools, such as Netstat(Citation: Netstat), in conjunction with [System Firmware](https://attack.mitre.org/techniques/T0857), then they can determine the role of certain devices on the network (Citation: MITRE). The adversary can also use [Network Sniffing](https://attack.mitre.org/techniques/T0842) to watch network traffic for details about the source, destination, protocol, and content. | https://attack.mitre.org/techniques/T0840 | 21 May 2020 | 29 March 2024 | ics-attack | 1.2 | Discovery |  | None | Command: Command Execution, Process: OS API Execution, Process: Process Creation, Script: Script Execution |  | (Citation: Anton Cherepanov, ESET June 2017),(Citation: Ben Hunter and Fred Gutierrez July 2020),,
T0842 | attack-pattern--38213338-1aab-479d-949b-c81b66ccca5c | Network Sniffing | Network sniffing is the practice of using a network interface on a computer system to monitor or capture information (Citation: Enterprise ATT&CK January 2018) regardless of whether it is the specified destination for the information. An adversary may attempt to sniff the traffic to gain information about the target. This information can vary in the level of importance. Relatively unimportant information is general communications to and from machines. Relatively important information would be login information. User credentials may be sent over an unencrypted protocol, such as Telnet, that can be captured and obtained through network packet analysis. In addition, ARP and Domain Name Service (DNS) poisoning can be used to capture credentials to websites, proxies, and internal systems by redirecting traffic to an adversary. | https://attack.mitre.org/techniques/T0842 | 21 May 2020 | 13 October 2023 | ics-attack | 1.0 | Discovery |  | None | Command: Command Execution, Process: Process Creation |  | (Citation: Carl Hurd March 2019),(Citation: Nicolas Falliere, Liam O Murchu, Eric Chien February 2011),(Citation: Wylie-22),(Citation: William Largent June 2018),(Citation: National Institute of Standards and Technology April 2013),(Citation: Keith Stouffer May 2015),
T0861 | attack-pattern--25852363-5968-4673-b81d-341d5ed90bd1 | Point & Tag Identification | Adversaries may collect point and tag values to gain a more comprehensive understanding of the process environment. Points may be values such as inputs, memory locations, outputs or other process specific variables. (Citation: Dennis L. Sloatman September 2016) Tags are the identifiers given to points for operator convenience. Collecting such tags provides valuable context to environmental points and enables an adversary to map inputs, outputs, and other values to their control processes. Understanding the points being collected may inform an adversary on which processes and values to keep track of over the course of an operation. | https://attack.mitre.org/techniques/T0861 | 21 May 2020 | 13 October 2023 | ics-attack | 1.1 | Collection |  | None | Application Log: Application Log Content, Network Traffic: Network Traffic Content | Jos Wetzels - Midnight Blue | (Citation: Daavid Hentunen, Antti Tikkanen June 2014),(Citation: CISA-AA22-103A),(Citation: ICS-CERT August 2018),(Citation: Dwight Anderson 2014),(Citation: Karen Scarfone; Paul Hoffman September 2009),(Citation: Department of Homeland Security September 2016),(Citation: Keith Stouffer May 2015),
T0843 | attack-pattern--be69c571-d746-4b1f-bdd0-c0c9817e9068 | Program Download | Adversaries may perform a program download to transfer a user program to a controller. Variations of program download, such as online edit and program append, allow a controller to continue running during the transfer and reconfiguration process without interruption to process control. However, before starting a full program download (i.e., download all) a controller may need to go into a stop state. This can have negative consequences on the physical process, especially if the controller is not able to fulfill a time-sensitive action. Adversaries may choose to avoid a download all in favor of an online edit or program append to avoid disrupting the physical process. An adversary may need to use the technique Detect Operating Mode or Change Operating Mode to make sure the controller is in the proper mode to accept a program download. The granularity of control to transfer a user program in whole or parts is dictated by the management protocol (e.g., S7CommPlus, TriStation) and underlying controller API. Thus, program download is a high-level term for the suite of vendor-specific API calls used to configure a controllers user program memory space. [Modify Controller Tasking](https://attack.mitre.org/techniques/T0821) and [Modify Program](https://attack.mitre.org/techniques/T0889) represent the configuration changes that are transferred to a controller via a program download. | https://attack.mitre.org/techniques/T0843 | 21 May 2020 | 13 October 2023 | ics-attack | 1.1 | Lateral Movement |  | None | Application Log: Application Log Content, Asset: Asset Inventory, Network Traffic: Network Traffic Content, Operational Databases: Device Alarm |  | (Citation: Nicolas Falliere, Liam O Murchu, Eric Chien February 2011),(Citation: Jos Wetzels January 2018),(Citation: FireEye TRITON Dec 2017),(Citation: Brubaker-Incontroller),(Citation: Spenneberg, Ralf, Maik Brggemann, and Hendrik Schwartke March 2016),(Citation: Wylie-22),(Citation: IEC February 2019),(Citation: Department of Homeland Security September 2016),
T0845 | attack-pattern--3067b85e-271e-4bc5-81ad-ab1a81d411e3 | Program Upload | Adversaries may attempt to upload a program from a PLC to gather information about an industrial process. Uploading a program may allow them to acquire and study the underlying logic. Methods of program upload include vendor software, which enables the user to upload and read a program running on a PLC. This software can be used to upload the target program to a workstation, jump box, or an interfacing device. | https://attack.mitre.org/techniques/T0845 | 21 May 2020 | 13 October 2023 | ics-attack | 1.0 | Collection |  | None | Application Log: Application Log Content, Network Traffic: Network Traffic Content, Network Traffic: Network Traffic Flow |  | (Citation: Wylie-22),(Citation: MDudek-ICS),(Citation: Brubaker-Incontroller),(Citation: Department of Homeland Security September 2016),
T0873 | attack-pattern--e72425f8-9ae6-41d3-bfdb-e1b865e60722 | Project File Infection | Adversaries may attempt to infect project files with malicious code. These project files may consist of objects, program organization units, variables such as tags, documentation, and other configurations needed for PLC programs to function. (Citation: Beckhoff) Using built in functions of the engineering software, adversaries may be able to download an infected program to a PLC in the operating environment enabling further [Execution](https://attack.mitre.org/tactics/TA0104) and [Persistence](https://attack.mitre.org/tactics/TA0110) techniques. (Citation: PLCdev) Adversaries may export their own code into project files with conditions to execute at specific intervals. (Citation: Nicolas Falliere, Liam O Murchu, Eric Chien February 2011) Malicious programs allow adversaries control of all aspects of the process enabled by the PLC. Once the project file is downloaded to a PLC the workstation device may be disconnected with the infected project file still executing. (Citation: PLCdev) | https://attack.mitre.org/techniques/T0873 | 21 May 2020 | 13 October 2023 | ics-attack | 1.0 | Persistence |  | None | File: File Modification |  | (Citation: Nicolas Falliere, Liam O Murchu, Eric Chien February 2011),(Citation: National Institute of Standards and Technology April 2013),
T0886 | attack-pattern--e1f9cdd2-9511-4fca-90d7-f3e92cfdd0bf | Remote Services | Adversaries may leverage remote services to move between assets and network segments. These services are often used to allow operators to interact with systems remotely within the network, some examples are RDP, SMB, SSH, and other similar mechanisms. (Citation: Blake Johnson, Dan Caban, Marina Krotofil, Dan Scali, Nathan Brubaker, Christopher Glyer December 2017) (Citation: Dragos December 2017) (Citation: Joe Slowik April 2019) Remote services could be used to support remote access, data transmission, authentication, name resolution, and other remote functions. Further, remote services may be necessary to allow operators and administrators to configure systems within the network from their engineering or management workstations. An adversary may use this technique to access devices which may be dual-homed (Citation: Blake Johnson, Dan Caban, Marina Krotofil, Dan Scali, Nathan Brubaker, Christopher Glyer December 2017) to multiple network segments, and can be used for [Program Download](https://attack.mitre.org/techniques/T0843) or to execute attacks on control devices directly through [Valid Accounts](https://attack.mitre.org/techniques/T0859). Specific remote services (RDP & VNC) may be a precursor to enable [Graphical User Interface](https://attack.mitre.org/techniques/T0823) execution on devices such as HMIs or engineering workstation software. Based on incident data, CISA and FBI assessed that Chinese state-sponsored actors also compromised various authorized remote access channels, including systems designed to transfer data and/or allow access between corporate and ICS networks. (Citation: CISA AA21-201A Pipeline Intrusion July 2021) | https://attack.mitre.org/techniques/T0886 | 12 April 2021 | 13 October 2023 | ics-attack | 1.1 | Initial Access, Lateral Movement |  | None | Command: Command Execution, Logon Session: Logon Session Creation, Module: Module Load, Network Share: Network Share Access, Network Traffic: Network Connection Creation, Network Traffic: Network Traffic Flow, Process: Process Creation | Daisuke Suzuki | (Citation: Nicolas Falliere, Liam O Murchu, Eric Chien February 2011),(Citation: Max Heinemeyer February 2020),(Citation: Andy Greenberg June 2017),(Citation: Brubaker-Incontroller),(Citation: FireEye TRITON 2018),(Citation: Triton-EENews-2017),(Citation: Dragos Crashoverride 2018),(Citation: Wylie-22),(Citation: Dragos-Pipedream),(Citation: North America Transmission Forum December 2019),
T0846 | attack-pattern--d5a69cfb-fc2a-46cb-99eb-74b236db5061 | Remote System Discovery | Adversaries may attempt to get a listing of other systems by IP address, hostname, or other logical identifier on a network that may be used for subsequent Lateral Movement or Discovery techniques. Functionality could exist within adversary tools to enable this, but utilities available on the operating system or vendor software could also be used. (Citation: Enterprise ATT&CK January 2018) | https://attack.mitre.org/techniques/T0846 | 21 May 2020 | 13 October 2023 | ics-attack | 1.1 | Discovery |  | None | File: File Access, Network Traffic: Network Traffic Content, Network Traffic: Network Traffic Flow, Process: Process Creation |  | (Citation: Anton Cherepanov, ESET June 2017),(Citation: CISA-AA22-103A),(Citation: Booz Allen Hamilton),(Citation: DHS CISA February 2019),(Citation: Julian Rrushi, Hassan Farhangi, Clay Howey, Kelly Carmichael, Joey Dabell December 2015),(Citation: Charles McLellan March 2016),(Citation: Spenneberg, Ralf, Maik Brggemann, and Hendrik Schwartke March 2016),(Citation: Wylie-22),(Citation: Dragos-Pipedream),(Citation: Aditya K Sood July 2019),(Citation: Langner November 2018),(Citation: Colin Gray),(Citation: Josh Rinaldi April 2016),(Citation: D. Parsons and D. Wylie September 2019),
T0888 | attack-pattern--2fedbe69-581f-447d-8a78-32ee7db939a9 | Remote System Information Discovery | An adversary may attempt to get detailed information about remote systems and their peripherals, such as make/model, role, and configuration. Adversaries may use information from Remote System Information Discovery to aid in targeting and shaping follow-on behaviors. For example, the system's operational role and model information can dictate whether it is a relevant target for the adversary's operational objectives. In addition, the system's configuration may be used to scope subsequent technique usage. Requests for system information are typically implemented using automation and management protocols and are often automatically requested by vendor software during normal operation. This information may be used to tailor management actions, such as program download and system or module firmware. An adversary may leverage this same information by issuing calls directly to the system's API. | https://attack.mitre.org/techniques/T0888 | 13 April 2021 | 13 October 2023 | ics-attack | 1.1 | Discovery |  | None | File: File Access, Network Traffic: Network Traffic Content, Network Traffic: Network Traffic Flow, Process: Process Creation |  | (Citation: Nicolas Falliere, Liam O Murchu, Eric Chien February 2011),(Citation: CISA-AA22-103A),(Citation: ESET Industroyer),(Citation: Industroyer2 Forescout July 2022),(Citation: Daavid Hentunen, Antti Tikkanen June 2014),(Citation: ICS-CERT August 2018),(Citation: Wylie-22),(Citation: Industroyer2 ESET April 2022),(Citation: Aditya K Sood July 2019),(Citation: Langner November 2018),(Citation: Colin Gray),(Citation: Josh Rinaldi April 2016),(Citation: D. Parsons and D. Wylie September 2019),
T0847 | attack-pattern--c267bbee-bb59-47fe-85e0-3ed210337c21 | Replication Through Removable Media | Adversaries may move onto systems, such as those separated from the enterprise network, by copying malware to removable media which is inserted into the control systems environment. The adversary may rely on unknowing trusted third parties, such as suppliers or contractors with access privileges, to introduce the removable media. This technique enables initial access to target devices that never connect to untrusted networks, but are physically accessible. Operators of the German nuclear power plant, Gundremmingen, discovered malware on a facility computer not connected to the internet. (Citation: Kernkraftwerk Gundremmingen April 2016) (Citation: Trend Micro April 2016) The malware included Conficker and W32.Ramnit, which were also found on eighteen removable disk drives in the facility. (Citation: Christoph Steitz, Eric Auchard April 2016) (Citation: Catalin Cimpanu April 2016) (Citation: Peter Dockrill April 2016) (Citation: Lee Mathews April 2016) (Citation: Sean Gallagher April 2016) (Citation: Dark Reading Staff April 2016) The plant has since checked for infection and cleaned up more than 1,000 computers. (Citation: BBC April 2016) An ESET researcher commented that internet disconnection does not guarantee system safety from infection or payload execution. (Citation: ESET April 2016) | https://attack.mitre.org/techniques/T0847 | 21 May 2020 | 13 October 2023 | ics-attack | 1.0 | Initial Access |  | None | Drive: Drive Creation, File: File Access, File: File Creation, Process: Process Creation |  | (Citation: Catalin Cimpanu April 2016),(Citation: Nicolas Falliere, Liam O Murchu, Eric Chien February 2011),(Citation: Symantec June 2015),(Citation: Langer Stuxnet),,
T0848 | attack-pattern--b14395bd-5419-4ef4-9bd8-696936f509bb | Rogue Master | Adversaries may setup a rogue master to leverage control server functions to communicate with outstations. A rogue master can be used to send legitimate control messages to other control system devices, affecting processes in unintended ways. It may also be used to disrupt network communications by capturing and receiving the network traffic meant for the actual master. Impersonating a master may also allow an adversary to avoid detection. In the case of the 2017 Dallas Siren incident, adversaries used a rogue master to send command messages to the 156 distributed sirens across the city, either through a single rogue transmitter with a strong signal, or using many distributed repeaters. (Citation: Bastille April 2017) (Citation: Zack Whittaker April 2017) | https://attack.mitre.org/techniques/T0848 | 21 May 2020 | 13 October 2023 | ics-attack | 1.2 | Initial Access |  | None | Application Log: Application Log Content, Asset: Asset Inventory, Network Traffic: Network Traffic Content, Network Traffic: Network Traffic Flow, Operational Databases: Device Alarm |  | (Citation: Marshall Abrams July 2008),(Citation: Dwight Anderson 2014),(Citation: Karen Scarfone; Paul Hoffman September 2009),(Citation: Department of Homeland Security September 2016),(Citation: Keith Stouffer May 2015),
T0851 | attack-pattern--3b6b9246-43f8-4c69-ad7a-2b11cfe0a0d9 | Rootkit | Adversaries may deploy rootkits to hide the presence of programs, files, network connections, services, drivers, and other system components. Rootkits are programs that hide the existence of malware by intercepting and modifying operating-system API calls that supply system information. Rootkits or rootkit-enabling functionality may reside at the user or kernel level in the operating system, or lower. (Citation: Enterprise ATT&CK January 2018) Firmware rootkits that affect the operating system yield nearly full control of the system. While firmware rootkits are normally developed for the main processing board, they can also be developed for the I/O that is attached to an asset. Compromise of this firmware allows the modification of all of the process variables and functions the module engages in. This may result in commands being disregarded and false information being fed to the main device. By tampering with device processes, an adversary may inhibit its expected response functions and possibly enable [Impact](https://attack.mitre.org/tactics/TA0105). | https://attack.mitre.org/techniques/T0851 | 21 May 2020 | 13 October 2023 | ics-attack | 1.1 | Evasion, Inhibit Response Function |  | None | Firmware: Firmware Modification |  | (Citation: Langer Stuxnet),(Citation: IEC February 2019),
T0852 | attack-pattern--c5e3cdbc-0387-4be9-8f83-ff5c0865f377 | Screen Capture | Adversaries may attempt to perform screen capture of devices in the control system environment. Screenshots may be taken of workstations, HMIs, or other devices that display environment-relevant process, device, reporting, alarm, or related data. These device displays may reveal information regarding the ICS process, layout, control, and related schematics. In particular, an HMI can provide a lot of important industrial process information. (Citation: ICS-CERT October 2017) Analysis of screen captures may provide the adversary with an understanding of intended operations and interactions between critical devices. | https://attack.mitre.org/techniques/T0852 | 21 May 2020 | 13 October 2023 | ics-attack | 1.0 | Collection |  | None | Command: Command Execution, Process: OS API Execution |  | (Citation: ICS-CERT October 2017),(Citation: Junnosuke Yagi March 2017),(Citation: Jacqueline O'Leary et al. September 2017),(Citation: Dragos),,
T0853 | attack-pattern--2dc2b567-8821-49f9-9045-8740f3d0b958 | Scripting | Adversaries may use scripting languages to execute arbitrary code in the form of a pre-written script or in the form of user-supplied code to an interpreter. Scripting languages are programming languages that differ from compiled languages, in that scripting languages use an interpreter, instead of a compiler. These interpreters read and compile part of the source code just before it is executed, as opposed to compilers, which compile each and every line of code to an executable file. Scripting allows software developers to run their code on any system where the interpreter exists. This way, they can distribute one package, instead of precompiling executables for many different systems. Scripting languages, such as Python, have their interpreters shipped as a default with many Linux distributions. In addition to being a useful tool for developers and administrators, scripting language interpreters may be abused by the adversary to execute code in the target environment. Due to the nature of scripting languages, this allows for weaponized code to be deployed to a target easily, and leaves open the possibility of on-the-fly scripting to perform a task. | https://attack.mitre.org/techniques/T0853 | 21 May 2020 | 13 October 2023 | ics-attack | 1.0 | Execution |  | None | Command: Command Execution, Module: Module Load, Process: Process Creation, Process: Process Metadata, Script: Script Execution |  | (Citation: Robert Falcone, Bryan Lee May 2016),(Citation: Tom Fakterman August 2019),(Citation: Symantec March 2019),(Citation: DHS CISA February 2019),(Citation: Mandiant-Sandworm-Ukraine-2022),(Citation: Dragos),(Citation: Dragos Crashoverride 2018),(Citation: FireEye TEMP.Veles 2018),,
T0881 | attack-pattern--063b5b92-5361-481a-9c3f-95492ed9a2d8 | Service Stop | Adversaries may stop or disable services on a system to render those services unavailable to legitimate users. Stopping critical services can inhibit or stop response to an incident or aid in the adversary's overall objectives to cause damage to the environment. (Citation: Enterprise ATT&CK) Services may not allow for modification of their data stores while running. Adversaries may stop services in order to conduct Data Destruction. (Citation: Enterprise ATT&CK) | https://attack.mitre.org/techniques/T0881 | 21 May 2020 | 13 October 2023 | ics-attack | 1.1 | Inhibit Response Function |  | None | Command: Command Execution, File: File Modification, Process: OS API Execution, Process: Process Creation, Process: Process Termination, Service: Service Metadata, Windows Registry: Windows Registry Key Modification |  | (Citation: Anton Cherepanov, ESET June 2017),(Citation: Ben Hunter and Fred Gutierrez July 2020),(Citation: Daniel Kapellmann Zafra, Keith Lunden, Nathan Brubaker, Jeremy Kennelly July 2020),(Citation: McAfee Labs October 2019),(Citation: Industroyer2 Mandiant April 2022),(Citation: Anton Cherepanov),(Citation: Department of Homeland Security September 2016),
T0865 | attack-pattern--648f995e-9c3a-41e4-aeee-98bb41037426 | Spearphishing Attachment | Adversaries may use a spearphishing attachment, a variant of spearphishing, as a form of a social engineering attack against specific targets. Spearphishing attachments are different from other forms of spearphishing in that they employ malware attached to an email. All forms of spearphishing are electronically delivered and target a specific individual, company, or industry. In this scenario, adversaries attach a file to the spearphishing email and usually rely upon [User Execution](https://attack.mitre.org/techniques/T0863) to gain execution and access. (Citation: Enterprise ATT&CK October 2019) A Chinese spearphishing campaign running from December 9, 2011 through February 29, 2012, targeted ONG organizations and their employees. The emails were constructed with a high level of sophistication to convince employees to open the malicious file attachments. (Citation: CISA AA21-201A Pipeline Intrusion July 2021) | https://attack.mitre.org/techniques/T0865 | 21 May 2020 | 13 October 2023 | ics-attack | 1.1 | Initial Access |  | None | Application Log: Application Log Content, File: File Creation, Network Traffic: Network Traffic Content, Process: Process Creation |  | (Citation: Jeff Jones May 2018),(Citation: Booz Allen Hamilton),(Citation: Robert Falcone, Bryan Lee May 2016),(Citation: Novetta Threat Research Group February 2016),(Citation: Daavid Hentunen, Antti Tikkanen June 2014),(Citation: Andy Greenburg June 2019),(Citation: Jacqueline O'Leary et al. September 2017),(Citation: Eduard Kovacs March 2018),,
T0856 | attack-pattern--8535b71e-3c12-4258-a4ab-40257a1becc4 | Spoof Reporting Message | Adversaries may spoof reporting messages in control system environments for evasion and to impair process control. In control systems, reporting messages contain telemetry data (e.g., I/O values) pertaining to the current state of equipment and the industrial process. Reporting messages are important for monitoring the normal operation of a system or identifying important events such as deviations from expected values. If an adversary has the ability to Spoof Reporting Messages, they can impact the control system in many ways. The adversary can Spoof Reporting Messages that state that the process is operating normally, as a form of evasion. The adversary could also Spoof Reporting Messages to make the defenders and operators think that other errors are occurring in order to distract them from the actual source of a problem. (Citation: Bonnie Zhu, Anthony Joseph, Shankar Sastry 2011) | https://attack.mitre.org/techniques/T0856 | 21 May 2020 | 13 October 2023 | ics-attack | 1.2 | Evasion, Impair Process Control |  | None | Network Traffic: Network Traffic Content, Network Traffic: Network Traffic Flow, Operational Databases: Device Alarm, Windows Registry: Windows Registry Key Modification |  | (Citation: Marshall Abrams July 2008),(Citation: Dwight Anderson 2014),(Citation: Karen Scarfone; Paul Hoffman September 2009),(Citation: Department of Homeland Security September 2016),(Citation: Keith Stouffer May 2015),
T0869 | attack-pattern--e076cca8-2f08-45c9-aff7-ea5ac798b387 | Standard Application Layer Protocol | Adversaries may establish command and control capabilities over commonly used application layer protocols such as HTTP(S), OPC, RDP, telnet, DNP3, and modbus. These protocols may be used to disguise adversary actions as benign network traffic. Standard protocols may be seen on their associated port or in some cases over a non-standard port. Adversaries may use these protocols to reach out of the network for command and control, or in some cases to other infected devices within the network. | https://attack.mitre.org/techniques/T0869 | 21 May 2020 | 13 October 2023 | ics-attack | 1.0 | Command and Control |  | None | Network Traffic: Network Traffic Content, Network Traffic: Network Traffic Flow |  | (Citation: Nicolas Falliere, Liam O Murchu, Eric Chien February 2011),(Citation: Jos Wetzels January 2018),(Citation: SecureWorks September 2019),(Citation: CISA-AA22-103A),(Citation: Booz Allen Hamilton),(Citation: Tom Fakterman August 2019),(Citation: Robert Falcone, Bryan Lee May 2016),,
T0862 | attack-pattern--5e0f75da-e108-4688-a6de-a4f07cc2cbe3 | Supply Chain Compromise | Adversaries may perform supply chain compromise to gain control systems environment access by means of infected products, software, and workflows. Supply chain compromise is the manipulation of products, such as devices or software, or their delivery mechanisms before receipt by the end consumer. Adversary compromise of these products and mechanisms is done for the goal of data or system compromise, once infected products are introduced to the target environment. Supply chain compromise can occur at all stages of the supply chain, from manipulation of development tools and environments to manipulation of developed products and tools distribution mechanisms. This may involve the compromise and replacement of legitimate software and patches, such as on third party or vendor websites. Targeting of supply chain compromise can be done in attempts to infiltrate the environments of a specific audience. In control systems environments with assets in both the IT and OT networks, it is possible a supply chain compromise affecting the IT environment could enable further access to the OT environment. Counterfeit devices may be introduced to the global supply chain posing safety and cyber risks to asset owners and operators. These devices may not meet the safety, engineering and manufacturing requirements of regulatory bodies but may feature tagging indicating conformance with industry standards. Due to the lack of adherence to standards and overall lesser quality, the counterfeit products may pose a serious safety and operational risk. (Citation: Control Global May 2019) Yokogawa identified instances in which their customers received counterfeit differential pressure transmitters using the Yokogawa logo. The counterfeit transmitters were nearly indistinguishable with a semblance of functionality and interface that mimics the genuine product. (Citation: Control Global May 2019) F-Secure Labs analyzed the approach the adversary used to compromise victim systems with Havex. (Citation: Daavid Hentunen, Antti Tikkanen June 2014) The adversary planted trojanized software installers available on legitimate ICS/SCADA vendor websites. After being downloaded, this software infected the host computer with a Remote Access Trojan (RAT). | https://attack.mitre.org/techniques/T0862 | 21 May 2020 | 13 October 2023 | ics-attack | 1.1 | Initial Access |  | None | File: File Metadata |  | (Citation: Dragos Threat Intelligence August 2019),(Citation: Daavid Hentunen, Antti Tikkanen June 2014),(Citation: Symantec Security Response July 2014),(Citation: Robert A. Martin January 2021),(Citation: OWASP),
T0894 | attack-pattern--1c5cf58c-a34a-40d7-82f4-f987cdfc2b91 | System Binary Proxy Execution | Adversaries may bypass process and/or signature-based defenses by proxying execution of malicious content with signed, or otherwise trusted, binaries. Binaries used in this technique are often Microsoft-signed files, indicating that they have been either downloaded from Microsoft or are already native in the operating system. (Citation: LOLBAS Project) Binaries signed with trusted digital certificates can typically execute on Windows systems protected by digital signature validation. Several Microsoft signed binaries that are default on Windows installations can be used to proxy execution of other files or commands. Similarly, on Linux systems adversaries may abuse trusted binaries such as split to proxy execution of malicious commands. (Citation: split man page)(Citation: GTFO split) Adversaries may abuse application binaries installed on a system for proxy execution of malicious code or domain-specific commands. These commands could be used to target local resources on the device or networked devices within the environment through defined APIs ([Execution through API](https://attack.mitre.org/techniques/T0871)) or application-specific programming languages (e.g., MicroSCADA SCIL). Application binaries may be signed by the developer or generally trusted by the operators, analysts, and monitoring tools accustomed to the environment. These applications may be developed and/or directly provided by the device vendor to enable configuration, management, and operation of their devices without many alternatives. Adversaries may seek to target these trusted application binaries to execute or send commands without the development of custom malware. For example, adversaries may target a SCADA server binary which has the existing ability to send commands to substation devices, such as through IEC 104 command messages. Proxy execution may still require the development of custom tools to hook into the application binary’s execution. | https://attack.mitre.org/techniques/T0894 | 25 March 2024 | 08 April 2024 | ics-attack | 1.0 | Evasion |  | None | Command: Command Execution, Process: Process Creation, Script: Script Execution |  | (Citation: Mandiant-Sandworm-Ukraine-2022),,
T0857 | attack-pattern--b9160e77-ea9e-4ba9-b1c8-53a3c466b13d | System Firmware | System firmware on modern assets is often designed with an update feature. Older device firmware may be factory installed and require special reprograming equipment. When available, the firmware update feature enables vendors to remotely patch bugs and perform upgrades. Device firmware updates are often delegated to the user and may be done using a software update package. It may also be possible to perform this task over the network. An adversary may exploit the firmware update feature on accessible devices to upload malicious or out-of-date firmware. Malicious modification of device firmware may provide an adversary with root access to a device, given firmware is one of the lowest programming abstraction layers. (Citation: Basnight, Zachry, et al.) | https://attack.mitre.org/techniques/T0857 | 21 May 2020 | 13 October 2023 | ics-attack | 1.1 | Inhibit Response Function, Persistence |  | None | Application Log: Application Log Content, Firmware: Firmware Modification, Network Traffic: Network Traffic Content, Operational Databases: Device Alarm |  | (Citation: DHS CISA February 2019),(Citation: Ukraine15 - EISAC - 201603),(Citation: Intel),(Citation: Department of Homeland Security September 2016),(Citation: ESET Research Whitepapers September 2018),(Citation: N/A),
T0882 | attack-pattern--b7e13ee8-182c-4f19-92a4-a88d7d855d54 | Theft of Operational Information | Adversaries may steal operational information on a production environment as a direct mission outcome for personal gain or to inform future operations. This information may include design documents, schedules, rotational data, or similar artifacts that provide insight on operations. In the Bowman Dam incident, adversaries probed systems for operational data. (Citation: Mark Thompson March 2016) (Citation: Danny Yadron December 2015) | https://attack.mitre.org/techniques/T0882 | 21 May 2020 | 13 October 2023 | ics-attack | 1.0 | Impact |  | None |  |  | (Citation: SecureWorks September 2019),(Citation: McAfee Labs October 2019),(Citation: Symantec),(Citation: Kevin Savage and Branko Spasojevic),(Citation: ESET),(Citation: National Institute of Standards and Technology April 2013),(Citation: Keith Stouffer May 2015),
T0864 | attack-pattern--35392fb4-a31d-4c6a-b9f2-1c65b7f5e6b9 | Transient Cyber Asset | Adversaries may target devices that are transient across ICS networks and external networks. Normally, transient assets are brought into an environment by authorized personnel and do not remain in that environment on a permanent basis. (Citation: North American Electric Reliability Corporation June 2021) Transient assets are commonly needed to support management functions and may be more common in systems where a remotely managed asset is not feasible, external connections for remote access do not exist, or 3rd party contractor/vendor access is required. Adversaries may take advantage of transient assets in different ways. For instance, adversaries may target a transient asset when it is connected to an external network and then leverage its trusted access in another environment to launch an attack. They may also take advantage of installed applications and libraries that are used by legitimate end-users to interact with control system devices. Transient assets, in some cases, may not be deployed with a secure configuration leading to weaknesses that could allow an adversary to propagate malicious executable code, e.g., the transient asset may be infected by malware and when connected to an ICS environment the malware propagates onto other systems. | https://attack.mitre.org/techniques/T0864 | 14 October 2021 | 13 October 2023 | ics-attack | 1.2 | Initial Access |  | None | Application Log: Application Log Content, Network Traffic: Network Traffic Flow |  | (Citation: Marshall Abrams July 2008),(Citation: North America Transmission Forum December 2019),(Citation: Emerson Exchange),(Citation: National Security Agency February 2016),(Citation: National Institute of Standards and Technology April 2013),
T0855 | attack-pattern--40b300ba-f553-48bf-862e-9471b220d455 | Unauthorized Command Message | Adversaries may send unauthorized command messages to instruct control system assets to perform actions outside of their intended functionality, or without the logical preconditions to trigger their expected function. Command messages are used in ICS networks to give direct instructions to control systems devices. If an adversary can send an unauthorized command message to a control system, then it can instruct the control systems device to perform an action outside the normal bounds of the device's actions. An adversary could potentially instruct a control systems device to perform an action that will cause an [Impact](https://attack.mitre.org/tactics/TA0105). (Citation: Bonnie Zhu, Anthony Joseph, Shankar Sastry 2011) In the Dallas Siren incident, adversaries were able to send command messages to activate tornado alarm systems across the city without an impending tornado or other disaster. (Citation: Zack Whittaker April 2017) (Citation: Benjamin Freed March 2019) | https://attack.mitre.org/techniques/T0855 | 21 May 2020 | 13 October 2023 | ics-attack | 1.2 | Impair Process Control |  | None | Application Log: Application Log Content, Network Traffic: Network Traffic Content, Network Traffic: Network Traffic Flow, Operational Databases: Process History/Live Data, Operational Databases: Process/Event Alarm |  | (Citation: Anton Cherepanov, ESET June 2017),(Citation: Marshall Abrams July 2008),(Citation: CISA-AA22-103A),(Citation: Ukraine15 - EISAC - 201603),(Citation: FireEye TRITON 2018),(Citation: Industroyer2 Mandiant April 2022),(Citation: Mandiant-Sandworm-Ukraine-2022),(Citation: Industroyer2 Forescout July 2022),(Citation: Dwight Anderson 2014),(Citation: Karen Scarfone; Paul Hoffman September 2009),(Citation: Department of Homeland Security September 2016),(Citation: Keith Stouffer May 2015),
T0863 | attack-pattern--2736b752-4ec5-4421-a230-8977dea7649c | User Execution | Adversaries may rely on a targeted organizations user interaction for the execution of malicious code. User interaction may consist of installing applications, opening email attachments, or granting higher permissions to documents. Adversaries may embed malicious code or visual basic code into files such as Microsoft Word and Excel documents or software installers. (Citation: Booz Allen Hamilton) Execution of this code requires that the user enable scripting or write access within the document. Embedded code may not always be noticeable to the user especially in cases of trojanized software. (Citation: Daavid Hentunen, Antti Tikkanen June 2014) A Chinese spearphishing campaign running from December 9, 2011 through February 29, 2012 delivered malware through spearphishing attachments which required user action to achieve execution. (Citation: CISA AA21-201A Pipeline Intrusion July 2021) | https://attack.mitre.org/techniques/T0863 | 21 May 2020 | 13 October 2023 | ics-attack | 1.1 | Execution |  | None | Application Log: Application Log Content, Command: Command Execution, File: File Access, Network Traffic: Network Connection Creation, Network Traffic: Network Traffic Content, Process: Process Creation |  | (Citation: Nicolas Falliere, Liam O Murchu, Eric Chien February 2011),(Citation: Kyle Wilhoit),(Citation: Tom Fakterman August 2019),(Citation: Orkhan Mamedov, Fedor Sinitsyn, Anton Ivanov October 2017),(Citation: Daavid Hentunen, Antti Tikkanen June 2014),,
T0859 | attack-pattern--cd2c76a4-5e23-4ca5-9c40-d5e0604f7101 | Valid Accounts | Adversaries may steal the credentials of a specific user or service account using credential access techniques. In some cases, default credentials for control system devices may be publicly available. Compromised credentials may be used to bypass access controls placed on various resources on hosts and within the network, and may even be used for persistent access to remote systems. Compromised and default credentials may also grant an adversary increased privilege to specific systems and devices or access to restricted areas of the network. Adversaries may choose not to use malware or tools, in conjunction with the legitimate access those credentials provide, to make it harder to detect their presence or to control devices and send legitimate commands in an unintended way. Adversaries may also create accounts, sometimes using predefined account names and passwords, to provide a means of backup access for persistence. (Citation: Booz Allen Hamilton) The overlap of credentials and permissions across a network of systems is of concern because the adversary may be able to pivot across accounts and systems to reach a high level of access (i.e., domain or enterprise administrator) and possibly between the enterprise and operational technology environments. Adversaries may be able to leverage valid credentials from one system to gain access to another system. | https://attack.mitre.org/techniques/T0859 | 21 May 2020 | 13 October 2023 | ics-attack | 1.1 | Lateral Movement, Persistence |  | None | Logon Session: Logon Session Creation, Logon Session: Logon Session Metadata, User Account: User Account Authentication |  | (Citation: CISA-AA22-103A),(Citation: Booz Allen Hamilton),(Citation: Ukraine15 - EISAC - 201603),(Citation: FireEye TRITON 2018),(Citation: Dragos),(Citation: Dragos Crashoverride 2018),(Citation: Wylie-22),(Citation: Schweitzer Engineering Laboratories August 2015),(Citation: Microsoft February 2019),(Citation: Microsoft May 2017),(Citation: Keith Stouffer May 2015),(Citation: Microsoft August 2018),(Citation: CISA June 2013),
T0860 | attack-pattern--2877063e-1851-48d2-bcc6-bc1d2733157e | Wireless Compromise | Adversaries may perform wireless compromise as a method of gaining communications and unauthorized access to a wireless network. Access to a wireless network may be gained through the compromise of a wireless device. (Citation: Alexander Bolshev, Gleb Cherbov July 2014) (Citation: Alexander Bolshev March 2014) Adversaries may also utilize radios and other wireless communication devices on the same frequency as the wireless network. Wireless compromise can be done as an initial access vector from a remote distance. A Polish student used a modified TV remote controller to gain access to and control over the Lodz city tram system in Poland. (Citation: John Bill May 2017) (Citation: Shelley Smith February 2008) The remote controller device allowed the student to interface with the trams network to modify track settings and override operator control. The adversary may have accomplished this by aligning the controller to the frequency and amplitude of IR control protocol signals. (Citation: Bruce Schneier January 2008) The controller then enabled initial access to the network, allowing the capture and replay of tram signals. (Citation: John Bill May 2017) | https://attack.mitre.org/techniques/T0860 | 21 May 2020 | 13 October 2023 | ics-attack | 1.2 | Initial Access |  | None | Application Log: Application Log Content, Logon Session: Logon Session Creation, Network Traffic: Network Traffic Flow | Scott Dougherty | (Citation: Marshall Abrams July 2008),(Citation: CISA March 2010),(Citation: DHS National Urban Security Technology Laboratory April 2019),
T0887 | attack-pattern--0fe075d5-beac-4d02-b93e-0f874997db72 | Wireless Sniffing | Adversaries may seek to capture radio frequency (RF) communication used for remote control and reporting in distributed environments. RF communication frequencies vary between 3 kHz to 300 GHz, although are commonly between 300 MHz to 6 GHz. (Citation: Candell, R., Hany, M., Lee, K. B., Liu,Y., Quimby, J., Remley, K. April 2018) The wavelength and frequency of the signal affect how the signal propagates through open air, obstacles (e.g. walls and trees) and the type of radio required to capture them. These characteristics are often standardized in the protocol and hardware and may have an effect on how the signal is captured. Some examples of wireless protocols that may be found in cyber-physical environments are: WirelessHART, Zigbee, WIA-FA, and 700 MHz Public Safety Spectrum. Adversaries may capture RF communications by using specialized hardware, such as software defined radio (SDR), handheld radio, or a computer with radio demodulator tuned to the communication frequency. (Citation: Bastille April 2017) Information transmitted over a wireless medium may be captured in-transit whether the sniffing device is the intended destination or not. This technique may be particularly useful to an adversary when the communications are not encrypted. (Citation: Gallagher, S. April 2017) In the 2017 Dallas Siren incident, it is suspected that adversaries likely captured wireless command message broadcasts on a 700 MHz frequency during a regular test of the system. These messages were later replayed to trigger the alarm systems. (Citation: Gallagher, S. April 2017) | https://attack.mitre.org/techniques/T0887 | 21 May 2020 | 13 October 2023 | ics-attack | 1.1 | Collection, Discovery |  | None | Network Traffic: Network Traffic Flow | ICSCoE Japan | ,(Citation: Bastille April 2017),(Citation: DHS National Urban Security Technology Laboratory April 2019),

## procedure examples
source ID | source name | source ref | source type | mapping type | target ID | target name | target ref | target type | mapping description | STIX ID | created | last modified
C0028 | 2015 Ukraine Electric Power Attack | campaign--46421788-b6e1-4256-b351-f8beffd1afba | campaign | uses | T0803 | Block Command Message | attack-pattern--008b8f56-6107-48be-aa9f-746f927dbb61 | technique | During the [2015 Ukraine Electric Power Attack](https://attack.mitre.org/campaigns/C0028), [Sandworm Team](https://attack.mitre.org/groups/G0034) blocked command messages by using malicious firmware to render serial-to-ethernet converters inoperable. (Citation: Ukraine15 - EISAC - 201603) | relationship--57510758-786a-4f0a-aab2-101eaf4e7b9f | 27 September 2023 | 04 October 2023
C0028 | 2015 Ukraine Electric Power Attack | campaign--46421788-b6e1-4256-b351-f8beffd1afba | campaign | uses | T0804 | Block Reporting Message | attack-pattern--3f1f4ccb-9be2-4ff8-8f69-dd972221169b | technique | During the [2015 Ukraine Electric Power Attack](https://attack.mitre.org/campaigns/C0028), [Sandworm Team](https://attack.mitre.org/groups/G0034) blocked reporting messages by using malicious firmware to render serial-to-ethernet converters inoperable. (Citation: Ukraine15 - EISAC - 201603) | relationship--9fb8c8ab-67de-42df-a82d-b6e45b82d949 | 27 September 2023 | 04 October 2023
C0028 | 2015 Ukraine Electric Power Attack | campaign--46421788-b6e1-4256-b351-f8beffd1afba | campaign | uses | T0805 | Block Serial COM | attack-pattern--1c478716-71d9-46a4-9a53-fa5d576adb60 | technique | During the [2015 Ukraine Electric Power Attack](https://attack.mitre.org/campaigns/C0028), [Sandworm Team](https://attack.mitre.org/groups/G0034) overwrote the serial-to-ethernet converter firmware, rendering the devices not operational. This meant that communication to the downstream serial devices was either not possible or more difficult. (Citation: Booz Allen Hamilton) | relationship--3fb86696-1d56-42d5-a73d-044a78b588fe | 27 September 2023 | 27 September 2023
C0028 | 2015 Ukraine Electric Power Attack | campaign--46421788-b6e1-4256-b351-f8beffd1afba | campaign | uses | T0885 | Commonly Used Port | attack-pattern--e6c31185-8040-4267-83d3-b217b8a92f07 | technique | During the [2015 Ukraine Electric Power Attack](https://attack.mitre.org/campaigns/C0028), [Sandworm Team](https://attack.mitre.org/groups/G0034) used port 443 to communicate with their C2 servers. (Citation: Booz Allen Hamilton) | relationship--6573327e-3757-424e-8570-04ffe7d5d0e2 | 27 September 2023 | 27 September 2023
C0028 | 2015 Ukraine Electric Power Attack | campaign--46421788-b6e1-4256-b351-f8beffd1afba | campaign | uses | T0884 | Connection Proxy | attack-pattern--d67adac8-e3b9-44f9-9e6d-6c2a7d69dbe4 | technique | During the [2015 Ukraine Electric Power Attack](https://attack.mitre.org/campaigns/C0028), [Sandworm Team](https://attack.mitre.org/groups/G0034) established an internal proxy prior to the installation of backdoors within the network. (Citation: Booz Allen Hamilton) | relationship--13d76624-7049-45c5-94d3-8f172b7f6336 | 27 September 2023 | 27 September 2023
C0028 | 2015 Ukraine Electric Power Attack | campaign--46421788-b6e1-4256-b351-f8beffd1afba | campaign | uses | T0813 | Denial of Control | attack-pattern--e33c7ecc-5a38-497f-beb2-a9a2049a4c20 | technique | During the [2015 Ukraine Electric Power Attack](https://attack.mitre.org/campaigns/C0028), [KillDisk](https://attack.mitre.org/software/S0607) rendered devices that were necessary for remote recovery unusable, including at least one RTU. Additionally, [Sandworm Team](https://attack.mitre.org/groups/G0034) overwrote the firmware for serial-to-ethernet converters, denying operators control of the downstream devices. (Citation: Booz Allen Hamilton)(Citation: Ukraine15 - EISAC - 201603) | relationship--97756c8a-b702-472b-8d67-15464a73093e | 27 September 2023 | 04 October 2023
C0028 | 2015 Ukraine Electric Power Attack | campaign--46421788-b6e1-4256-b351-f8beffd1afba | campaign | uses | T0814 | Denial of Service | attack-pattern--1b22b676-9347-4c55-9a35-ef0dc653db5b | technique | During the [2015 Ukraine Electric Power Attack](https://attack.mitre.org/campaigns/C0028), power company phone line operators were hit with a denial of service attack so that they couldn’t field customers’ calls about outages. Operators were also denied service to their downstream devices when their serial-to-ethernet converters had their firmware overwritten, which bricked the devices. (Citation: Ukraine15 - EISAC - 201603) | relationship--7d752615-33f0-44ed-a156-25d84f384e75 | 27 September 2023 | 04 October 2023
C0028 | 2015 Ukraine Electric Power Attack | campaign--46421788-b6e1-4256-b351-f8beffd1afba | campaign | uses | T0816 | Device Restart/Shutdown | attack-pattern--25dfc8ad-bd73-4dfd-84a9-3c3d383f76e9 | technique | During the [2015 Ukraine Electric Power Attack](https://attack.mitre.org/campaigns/C0028), [Sandworm Team](https://attack.mitre.org/groups/G0034) scheduled the uninterruptable power supplies (UPS) to shutdown data and telephone servers via the UPS management interface. (Citation: Ukraine15 - EISAC - 201603)(Citation: Booz Allen Hamilton) | relationship--8b7403f5-90d2-4d2c-a484-87d29f419a9f | 27 September 2023 | 04 October 2023
C0028 | 2015 Ukraine Electric Power Attack | campaign--46421788-b6e1-4256-b351-f8beffd1afba | campaign | uses | T0822 | External Remote Services | attack-pattern--8d2f3bab-507c-4424-b58b-edc977bd215c | technique | During the [2015 Ukraine Electric Power Attack](https://attack.mitre.org/campaigns/C0028), [Sandworm Team](https://attack.mitre.org/groups/G0034) used Valid Accounts taken from the Windows Domain Controller to access the control system Virtual Private Network (VPN) used by grid operators. (Citation: Booz Allen Hamilton) | relationship--00b9e63b-57a7-408e-83d6-fc03535010a6 | 27 September 2023 | 27 September 2023
C0028 | 2015 Ukraine Electric Power Attack | campaign--46421788-b6e1-4256-b351-f8beffd1afba | campaign | uses | T0823 | Graphical User Interface | attack-pattern--b0628bfc-5376-4a38-9182-f324501cb4cf | technique | During the [2015 Ukraine Electric Power Attack](https://attack.mitre.org/campaigns/C0028), [Sandworm Team](https://attack.mitre.org/groups/G0034) utilized HMI GUIs in the SCADA environment to open breakers. (Citation: Ukraine15 - EISAC - 201603) | relationship--8d0d6365-7bc0-417d-9268-c7c31fcb0d91 | 27 September 2023 | 04 October 2023
C0028 | 2015 Ukraine Electric Power Attack | campaign--46421788-b6e1-4256-b351-f8beffd1afba | campaign | uses | T0867 | Lateral Tool Transfer | attack-pattern--ead7bd34-186e-4c79-9a4d-b65bcce6ed9d | technique | During the [2015 Ukraine Electric Power Attack](https://attack.mitre.org/campaigns/C0028), [Sandworm Team](https://attack.mitre.org/groups/G0034) moved their tools laterally within the ICS network. (Citation: Booz Allen Hamilton) | relationship--8a86ad59-dff1-46dc-8ffd-3c62b96c6e62 | 27 September 2023 | 27 September 2023
C0028 | 2015 Ukraine Electric Power Attack | campaign--46421788-b6e1-4256-b351-f8beffd1afba | campaign | uses | T0826 | Loss of Availability | attack-pattern--b5b9bacb-97f2-4249-b804-47fd44de1f95 | technique | During the [2015 Ukraine Electric Power Attack](https://attack.mitre.org/campaigns/C0028), [Sandworm Team](https://attack.mitre.org/groups/G0034) opened the breakers at the infected sites, shutting the power off for thousands of businesses and households for around 6 hours. (Citation: Ukraine15 - EISAC - 201603)(Citation: Booz Allen Hamilton) | relationship--f7c5bd1b-c596-41b2-b415-2bf5179667df | 27 September 2023 | 04 October 2023
C0028 | 2015 Ukraine Electric Power Attack | campaign--46421788-b6e1-4256-b351-f8beffd1afba | campaign | uses | T0827 | Loss of Control | attack-pattern--a81696ef-c106-482c-8f80-59c30f2569fb | technique | During the [2015 Ukraine Electric Power Attack](https://attack.mitre.org/campaigns/C0028), operators were shut out of their equipment either through the denial of peripheral use or the degradation of equipment. Operators were therefore unable to recover from the incident through their traditional means. Much of the power was restored manually. (Citation: Ukraine15 - EISAC - 201603) | relationship--d1388bba-9869-4e3e-a6c9-430784ad924d | 27 September 2023 | 04 October 2023
C0028 | 2015 Ukraine Electric Power Attack | campaign--46421788-b6e1-4256-b351-f8beffd1afba | campaign | uses | T0828 | Loss of Productivity and Revenue | attack-pattern--63b6942d-8359-4506-bfb3-cf87aa8120ee | technique | During the [2015 Ukraine Electric Power Attack](https://attack.mitre.org/campaigns/C0028), power breakers were opened which caused the operating companies to be unable to deliver power, and left thousands of businesses and households without power for around 6 hours. (Citation: Ukraine15 - EISAC - 201603)(Citation: Booz Allen Hamilton) | relationship--423271c0-04dc-42d0-8e27-fb0b6067e096 | 27 September 2023 | 04 October 2023
C0028 | 2015 Ukraine Electric Power Attack | campaign--46421788-b6e1-4256-b351-f8beffd1afba | campaign | uses | T0831 | Manipulation of Control | attack-pattern--1af9e3fd-2bcc-414d-adbd-fe3b95c02ca1 | technique | During the [2015 Ukraine Electric Power Attack](https://attack.mitre.org/campaigns/C0028), [Sandworm Team](https://attack.mitre.org/groups/G0034) opened live breakers via remote commands to the HMI, causing blackouts. (Citation: Ukraine15 - EISAC - 201603) | relationship--4f83cc15-274d-44c6-859f-e598e362e76e | 27 September 2023 | 04 October 2023
C0028 | 2015 Ukraine Electric Power Attack | campaign--46421788-b6e1-4256-b351-f8beffd1afba | campaign | uses | T0886 | Remote Services | attack-pattern--e1f9cdd2-9511-4fca-90d7-f3e92cfdd0bf | technique | During the [2015 Ukraine Electric Power Attack](https://attack.mitre.org/campaigns/C0028), [Sandworm Team](https://attack.mitre.org/groups/G0034) used an IT helpdesk software to move the mouse on ICS control devices to maliciously release electricity breakers. (Citation: Andy Greenberg June 2017) | relationship--352ed52c-88ba-4731-a917-4c33da0f29d4 | 27 September 2023 | 27 September 2023
C0028 | 2015 Ukraine Electric Power Attack | campaign--46421788-b6e1-4256-b351-f8beffd1afba | campaign | uses | T0846 | Remote System Discovery | attack-pattern--d5a69cfb-fc2a-46cb-99eb-74b236db5061 | technique | During the [2015 Ukraine Electric Power Attack](https://attack.mitre.org/campaigns/C0028), [Sandworm Team](https://attack.mitre.org/groups/G0034) remotely discovered operational assets once on the OT network. (Citation: Charles McLellan March 2016) (Citation: Booz Allen Hamilton) | relationship--a57b233b-6613-4f78-aa48-e85518aaa7cf | 27 September 2023 | 27 September 2023
C0028 | 2015 Ukraine Electric Power Attack | campaign--46421788-b6e1-4256-b351-f8beffd1afba | campaign | uses | T0857 | System Firmware | attack-pattern--b9160e77-ea9e-4ba9-b1c8-53a3c466b13d | technique | During the [2015 Ukraine Electric Power Attack](https://attack.mitre.org/campaigns/C0028), [Sandworm Team](https://attack.mitre.org/groups/G0034) overwrote the serial-to-ethernet gateways with custom firmware to make systems either disabled, shutdown, and/or unrecoverable. (Citation: Ukraine15 - EISAC - 201603) | relationship--24885921-734f-46c1-85d7-3f79e0b886d6 | 27 September 2023 | 04 October 2023
C0028 | 2015 Ukraine Electric Power Attack | campaign--46421788-b6e1-4256-b351-f8beffd1afba | campaign | uses | T0855 | Unauthorized Command Message | attack-pattern--40b300ba-f553-48bf-862e-9471b220d455 | technique | During the [2015 Ukraine Electric Power Attack](https://attack.mitre.org/campaigns/C0028), [Sandworm Team](https://attack.mitre.org/groups/G0034) issued unauthorized commands to substation breaks after gaining control of operator workstations and accessing a distribution management system (DMS) application. (Citation: Ukraine15 - EISAC - 201603) | relationship--acace658-da7e-4a19-aa98-8aec8c966dde | 27 September 2023 | 04 October 2023
C0028 | 2015 Ukraine Electric Power Attack | campaign--46421788-b6e1-4256-b351-f8beffd1afba | campaign | uses | T0859 | Valid Accounts | attack-pattern--cd2c76a4-5e23-4ca5-9c40-d5e0604f7101 | technique | During the [2015 Ukraine Electric Power Attack](https://attack.mitre.org/campaigns/C0028), [Sandworm Team](https://attack.mitre.org/groups/G0034) used valid accounts to laterally move through VPN connections and dual-homed systems. Sandworm Team used the credentials of valid accounts to interact with client applications and access employee workstations hosting HMI applications. (Citation: Ukraine15 - EISAC - 201603)(Citation: Booz Allen Hamilton) | relationship--2f0d1a71-7cb6-4979-b072-a859d117d47f | 27 September 2023 | 04 October 2023
C0025 | 2016 Ukraine Electric Power Attack | campaign--aa73efef-1418-4dbe-b43c-87a498e97234 | campaign | uses | T0807 | Command-Line Interface | attack-pattern--24a9253e-8948-4c98-b751-8e2aee53127c | technique | During the [2016 Ukraine Electric Power Attack](https://attack.mitre.org/campaigns/C0025), [Sandworm Team](https://attack.mitre.org/groups/G0034) supplied the name of the payload DLL to [Industroyer](https://attack.mitre.org/software/S0604) via a command line parameter.(Citation: ESET Industroyer) | relationship--b07e6896-a840-49a1-8d58-94396a902b95 | 31 March 2023 | 31 March 2023
C0025 | 2016 Ukraine Electric Power Attack | campaign--aa73efef-1418-4dbe-b43c-87a498e97234 | campaign | uses | T0867 | Lateral Tool Transfer | attack-pattern--ead7bd34-186e-4c79-9a4d-b65bcce6ed9d | technique | During the [2016 Ukraine Electric Power Attack](https://attack.mitre.org/campaigns/C0025), [Sandworm Team](https://attack.mitre.org/groups/G0034) used a VBS script to facilitate lateral tool transfer. The VBS script was used to copy ICS-specific payloads with the following command: `cscript C:\Backinfo\ufn.vbs C:\Backinfo\101.dll C:\Delta\101.dll`(Citation: Dragos Crashoverride 2018) | relationship--49966e16-04a2-4fd7-86cd-aa934040a9d8 | 31 March 2023 | 07 April 2023
C0025 | 2016 Ukraine Electric Power Attack | campaign--aa73efef-1418-4dbe-b43c-87a498e97234 | campaign | uses | T0849 | Masquerading | attack-pattern--ba203963-3182-41ac-af14-7e7ebc83cd61 | technique | During the [2016 Ukraine Electric Power Attack](https://attack.mitre.org/campaigns/C0025), [Sandworm Team](https://attack.mitre.org/groups/G0034) transferred executable files as .txt and then renamed them to .exe, likely to avoid detection through extension tracking.(Citation: Dragos Crashoverride 2018) | relationship--e156609f-c30b-4bf5-8a1b-9689ba778a14 | 31 March 2023 | 07 April 2023
C0025 | 2016 Ukraine Electric Power Attack | campaign--aa73efef-1418-4dbe-b43c-87a498e97234 | campaign | uses | T0886 | Remote Services | attack-pattern--e1f9cdd2-9511-4fca-90d7-f3e92cfdd0bf | technique | During the [2016 Ukraine Electric Power Attack](https://attack.mitre.org/campaigns/C0025), [Sandworm Team](https://attack.mitre.org/groups/G0034) used MS-SQL access to a pivot machine, allowing code execution throughout the ICS network.(Citation: Dragos Crashoverride 2018) | relationship--4b98b72c-a093-4917-a21b-a0b4f388e98e | 31 March 2023 | 07 April 2023
C0025 | 2016 Ukraine Electric Power Attack | campaign--aa73efef-1418-4dbe-b43c-87a498e97234 | campaign | uses | T0853 | Scripting | attack-pattern--2dc2b567-8821-49f9-9045-8740f3d0b958 | technique | During the [2016 Ukraine Electric Power Attack](https://attack.mitre.org/campaigns/C0025), [Sandworm Team](https://attack.mitre.org/groups/G0034) utilized VBS and batch scripts for file movement and as wrappers for PowerShell execution.(Citation: Dragos Crashoverride 2018) | relationship--7bd6e5e4-6614-41ed-8a84-8eb633a91e07 | 31 March 2023 | 07 April 2023
C0025 | 2016 Ukraine Electric Power Attack | campaign--aa73efef-1418-4dbe-b43c-87a498e97234 | campaign | uses | T0859 | Valid Accounts | attack-pattern--cd2c76a4-5e23-4ca5-9c40-d5e0604f7101 | technique | During the [2016 Ukraine Electric Power Attack](https://attack.mitre.org/campaigns/C0025), [Sandworm Team](https://attack.mitre.org/groups/G0034) used valid accounts to laterally move through VPN connections and dual-homed systems.(Citation: Dragos Crashoverride 2018) | relationship--a6479493-6154-408f-90df-9d2f3ae352d1 | 31 March 2023 | 07 April 2023
C0034 | 2022 Ukraine Electric Power Attack | campaign--df8eb785-70f8-4300-b444-277ba849083d | campaign | uses | T0895 | Autorun Image | attack-pattern--77d9c726-b53e-481d-8bcc-1068aebfbb9d | technique | During the [2022 Ukraine Electric Power Attack](https://attack.mitre.org/campaigns/C0034), [Sandworm Team](https://attack.mitre.org/groups/G0034) used existing hypervisor access to map an ISO image named `a.iso` to a virtual machine running a SCADA server. The SCADA server’s operating system was configured to autorun CD-ROM images, and as a result, a malicious VBS script on the ISO image was automatically executed.(Citation: Mandiant-Sandworm-Ukraine-2022) | relationship--d4da5e90-7986-4c8a-bfb6-df4c0586ce87 | 27 March 2024 | 17 April 2024
C0034 | 2022 Ukraine Electric Power Attack | campaign--df8eb785-70f8-4300-b444-277ba849083d | campaign | uses | T0807 | Command-Line Interface | attack-pattern--24a9253e-8948-4c98-b751-8e2aee53127c | technique | During the [2022 Ukraine Electric Power Attack](https://attack.mitre.org/campaigns/C0034), [Sandworm Team](https://attack.mitre.org/groups/G0034) leveraged the SCIL-API on the MicroSCADA platform to execute commands through the `scilc.exe` binary.(Citation: Mandiant-Sandworm-Ukraine-2022) | relationship--df88d021-cb8e-482d-9260-445d0a0244ac | 27 March 2024 | 17 April 2024
C0034 | 2022 Ukraine Electric Power Attack | campaign--df8eb785-70f8-4300-b444-277ba849083d | campaign | uses | T0853 | Scripting | attack-pattern--2dc2b567-8821-49f9-9045-8740f3d0b958 | technique | During the [2022 Ukraine Electric Power Attack](https://attack.mitre.org/campaigns/C0034), [Sandworm Team](https://attack.mitre.org/groups/G0034) utilizes a Visual Basic script `lun.vbs` to execute `n.bat` which then executed the MicroSCADA `scilc.exe` command.(Citation: Mandiant-Sandworm-Ukraine-2022) | relationship--43b11545-3b70-4284-a369-bed7a0de4fd0 | 27 March 2024 | 17 April 2024
C0034 | 2022 Ukraine Electric Power Attack | campaign--df8eb785-70f8-4300-b444-277ba849083d | campaign | uses | T0894 | System Binary Proxy Execution | attack-pattern--1c5cf58c-a34a-40d7-82f4-f987cdfc2b91 | technique | During the [2022 Ukraine Electric Power Attack](https://attack.mitre.org/campaigns/C0034), [Sandworm Team](https://attack.mitre.org/groups/G0034) executed a MicroSCADA application binary `scilc.exe` to send a predefined list of SCADA instructions specified in a file defined by the adversary, `s1.txt`. The executed command `C:\sc\prog\exec\scilc.exe -do pack\scil\s1.txt` leverages the SCADA software to send unauthorized command messages to remote substations.(Citation: Mandiant-Sandworm-Ukraine-2022) | relationship--984d517f-56a1-4eb4-95e5-994eb9c6c3b5 | 27 March 2024 | 17 April 2024
C0034 | 2022 Ukraine Electric Power Attack | campaign--df8eb785-70f8-4300-b444-277ba849083d | campaign | uses | T0855 | Unauthorized Command Message | attack-pattern--40b300ba-f553-48bf-862e-9471b220d455 | technique | During the [2022 Ukraine Electric Power Attack](https://attack.mitre.org/campaigns/C0034), [Sandworm Team](https://attack.mitre.org/groups/G0034) used the MicroSCADA SCIL-API to specify a set of SCADA instructions, including the sending of unauthorized commands to substation devices.(Citation: Mandiant-Sandworm-Ukraine-2022) | relationship--7cd47eb6-e73a-4a0b-a62e-7e066090b804 | 27 March 2024 | 17 April 2024
C0020 | Maroochy Water Breach | campaign--70cab19e-1745-425e-b3db-c02cd5ff157a | campaign | uses | T0878 | Alarm Suppression | attack-pattern--2900bbd8-308a-4274-b074-5b8bde8347bc | technique | In the [Maroochy Water Breach](https://attack.mitre.org/campaigns/C0020), the adversary suppressed alarm reporting to the central computer.(Citation: Marshall Abrams July 2008) | relationship--c1154a56-6f5f-4760-8b34-79b0e8a79c1f | 10 March 2023 | 10 March 2023
C0020 | Maroochy Water Breach | campaign--70cab19e-1745-425e-b3db-c02cd5ff157a | campaign | uses | T0879 | Damage to Property | attack-pattern--83ebd22f-b401-4d59-8219-2294172cf916 | technique | In the [Maroochy Water Breach](https://attack.mitre.org/campaigns/C0020), the adversary gained remote computer access to the control system and altered data so that whatever function should have occurred at affected pumping stations did not occur or occurred in a different way. This ultimately led to 800,000 liters of raw sewage being spilled out into the community. The raw sewage affected local parks, rivers, and even a local hotel. This resulted in harm to marine life and produced a sickening stench from the community's affected rivers.(Citation: Marshall Abrams July 2008) | relationship--642cae89-bb5c-46f3-9fea-8d747b930c35 | 10 March 2023 | 05 April 2023
C0020 | Maroochy Water Breach | campaign--70cab19e-1745-425e-b3db-c02cd5ff157a | campaign | uses | T0813 | Denial of Control | attack-pattern--e33c7ecc-5a38-497f-beb2-a9a2049a4c20 | technique | In the [Maroochy Water Breach](https://attack.mitre.org/campaigns/C0020), the adversary temporarily shut an investigator out of the network preventing them from issuing any controls.(Citation: Marshall Abrams July 2008) | relationship--adf2072c-0341-4fc2-9d25-495b4af864e9 | 10 March 2023 | 10 March 2023
C0020 | Maroochy Water Breach | campaign--70cab19e-1745-425e-b3db-c02cd5ff157a | campaign | uses | T0815 | Denial of View | attack-pattern--56ddc820-6cfb-407f-850b-52c035d123ac | technique | In the [Maroochy Water Breach](https://attack.mitre.org/campaigns/C0020), the adversary temporarily shut an investigator out of the network, preventing them from viewing the state of the system.(Citation: Marshall Abrams July 2008) | relationship--e0da1f92-82b1-4096-86c4-1aef58ca89fb | 10 March 2023 | 10 March 2023
C0020 | Maroochy Water Breach | campaign--70cab19e-1745-425e-b3db-c02cd5ff157a | campaign | uses | T0822 | External Remote Services | attack-pattern--8d2f3bab-507c-4424-b58b-edc977bd215c | technique | In the [Maroochy Water Breach](https://attack.mitre.org/campaigns/C0020), the adversary gained remote computer access to the system over radio.(Citation: Marshall Abrams July 2008) | relationship--245c8c36-28e5-4508-a585-7768cb33299a | 10 March 2023 | 10 March 2023
C0020 | Maroochy Water Breach | campaign--70cab19e-1745-425e-b3db-c02cd5ff157a | campaign | uses | T0838 | Modify Alarm Settings | attack-pattern--e5de767e-f513-41cd-aa15-33f6ce5fbf92 | technique | In the [Maroochy Water Breach](https://attack.mitre.org/campaigns/C0020), the adversary disabled alarms at four pumping stations, preventing notifications to the central computer.(Citation: Marshall Abrams July 2008) | relationship--268b9429-b1c6-4bc3-84cf-8512e8ef57a7 | 10 March 2023 | 05 April 2023
C0020 | Maroochy Water Breach | campaign--70cab19e-1745-425e-b3db-c02cd5ff157a | campaign | uses | T0836 | Modify Parameter | attack-pattern--097924ce-a9a9-4039-8591-e0deedfb8722 | technique | In the [Maroochy Water Breach](https://attack.mitre.org/campaigns/C0020), the adversary gained remote computer access to the control system and altered data so that whatever function should have occurred at affected pumping stations did not occur or occurred in a different way. The software program installed in the laptop was one developed for changing configurations in the PDS computers. This ultimately led to 800,000 liters of raw sewage being spilled out into the community.(Citation: Marshall Abrams July 2008) | relationship--668f8c4b-225a-4287-ac5b-7717a4f75b5d | 10 March 2023 | 10 March 2023
C0020 | Maroochy Water Breach | campaign--70cab19e-1745-425e-b3db-c02cd5ff157a | campaign | uses | T0848 | Rogue Master | attack-pattern--b14395bd-5419-4ef4-9bd8-696936f509bb | technique | In the [Maroochy Water Breach](https://attack.mitre.org/campaigns/C0020), the adversary falsified network addresses in order to send false data and instructions to pumping stations.(Citation: Marshall Abrams July 2008) | relationship--b4efcbe0-ffe3-4d9a-8dba-570e68494af1 | 10 March 2023 | 10 March 2023
C0020 | Maroochy Water Breach | campaign--70cab19e-1745-425e-b3db-c02cd5ff157a | campaign | uses | T0856 | Spoof Reporting Message | attack-pattern--8535b71e-3c12-4258-a4ab-40257a1becc4 | technique | In the [Maroochy Water Breach](https://attack.mitre.org/campaigns/C0020), the adversary used a dedicated analog two-way radio system to send false data and instructions to pumping stations and the central computer.(Citation: Marshall Abrams July 2008) | relationship--6e329090-fc8c-4a7f-bbf9-08067ad9ebe5 | 10 March 2023 | 10 March 2023
C0020 | Maroochy Water Breach | campaign--70cab19e-1745-425e-b3db-c02cd5ff157a | campaign | uses | T0864 | Transient Cyber Asset | attack-pattern--35392fb4-a31d-4c6a-b9f2-1c65b7f5e6b9 | technique | In the [Maroochy Water Breach](https://attack.mitre.org/campaigns/C0020), the adversary utilized a computer, possibly stolen, with proprietary engineering software to communicate with a wastewater system.(Citation: Marshall Abrams July 2008) | relationship--59cb471f-ad8b-464f-ab8f-c267f329b0dc | 10 March 2023 | 10 March 2023
C0020 | Maroochy Water Breach | campaign--70cab19e-1745-425e-b3db-c02cd5ff157a | campaign | uses | T0855 | Unauthorized Command Message | attack-pattern--40b300ba-f553-48bf-862e-9471b220d455 | technique | In the [Maroochy Water Breach](https://attack.mitre.org/campaigns/C0020), the adversary used a dedicated analog two-way radio system to send false data and instructions to pumping stations and the central computer.(Citation: Marshall Abrams July 2008) | relationship--c2484b15-7dd0-4280-8898-a6a7da6f0ca2 | 10 March 2023 | 10 March 2023
C0020 | Maroochy Water Breach | campaign--70cab19e-1745-425e-b3db-c02cd5ff157a | campaign | uses | T0860 | Wireless Compromise | attack-pattern--2877063e-1851-48d2-bcc6-bc1d2733157e | technique | In the [Maroochy Water Breach](https://attack.mitre.org/campaigns/C0020), the adversary used a two-way radio to communicate with and set the frequencies of Maroochy Shire's repeater stations.(Citation: Marshall Abrams July 2008) | relationship--ae7ed6d8-65cc-45a0-82c3-c28e5630bf7c | 10 March 2023 | 10 March 2023
C0030 | Triton Safety Instrumented System Attack | campaign--45a98f02-852f-49b2-94c0-c63207bebbbf | campaign | uses | T0830 | Adversary-in-the-Middle | attack-pattern--9a505987-ab05-4f46-a9a6-6441442eec3b | technique | In the [Triton Safety Instrumented System Attack](https://attack.mitre.org/campaigns/C0030), [TEMP.Veles](https://attack.mitre.org/groups/G0088) changed phone numbers tied to certain specific accounts in a designated contact list. They then used the changed phone numbers to redirect network traffic to websites controlled by them, thereby allowing them to capture and use any login codes sent to the devices via text message.(Citation: Triton-EENews-2017) | relationship--03b4dae7-3b20-4ea9-9f7c-6c97582f98b7 | 28 March 2024 | 10 April 2024
C0030 | Triton Safety Instrumented System Attack | campaign--45a98f02-852f-49b2-94c0-c63207bebbbf | campaign | uses | T0807 | Command-Line Interface | attack-pattern--24a9253e-8948-4c98-b751-8e2aee53127c | technique | In the [Triton Safety Instrumented System Attack](https://attack.mitre.org/campaigns/C0030), [TEMP.Veles](https://attack.mitre.org/groups/G0088)’ tool took one option from the command line, which was a single IP address of the target Triconex device.(Citation: FireEye TRITON Dec 2017) | relationship--3a04717f-b74c-4096-b031-ee7115fdc3c9 | 28 March 2024 | 10 April 2024
C0030 | Triton Safety Instrumented System Attack | campaign--45a98f02-852f-49b2-94c0-c63207bebbbf | campaign | uses | T0872 | Indicator Removal on Host | attack-pattern--53a26eee-1080-4d17-9762-2027d5a1b805 | technique | In the [Triton Safety Instrumented System Attack](https://attack.mitre.org/campaigns/C0030), [TEMP.Veles](https://attack.mitre.org/groups/G0088) would programmatically return the controller to a normal running state if the [Triton](https://attack.mitre.org/software/S1009) malware failed. If the controller could not recover in a defined time window, [TEMP.Veles](https://attack.mitre.org/groups/G0088) programmatically overwrote their malicious program with invalid data.(Citation: FireEye TRITON Dec 2017) | relationship--b05d678b-4d87-4261-9366-f8b757a77661 | 28 March 2024 | 10 April 2024
C0030 | Triton Safety Instrumented System Attack | campaign--45a98f02-852f-49b2-94c0-c63207bebbbf | campaign | uses | T0867 | Lateral Tool Transfer | attack-pattern--ead7bd34-186e-4c79-9a4d-b65bcce6ed9d | technique | In the [Triton Safety Instrumented System Attack](https://attack.mitre.org/campaigns/C0030), [TEMP.Veles](https://attack.mitre.org/groups/G0088) made attempts on multiple victim machines to transfer and execute the WMImplant tool.(Citation: FireEye TEMP.Veles 2018) | relationship--c137fcd2-ce51-4e17-9c2f-f1aaf9b64ce7 | 28 March 2024 | 10 April 2024
C0030 | Triton Safety Instrumented System Attack | campaign--45a98f02-852f-49b2-94c0-c63207bebbbf | campaign | uses | T0828 | Loss of Productivity and Revenue | attack-pattern--63b6942d-8359-4506-bfb3-cf87aa8120ee | technique | In the [Triton Safety Instrumented System Attack](https://attack.mitre.org/campaigns/C0030), [TEMP.Veles](https://attack.mitre.org/groups/G0088) tripped a controller into a failed safe state, which caused an automatic shutdown of the plant, this resulted in a pause of plant operations for more than a week. Thereby impacting industrial processes and halting productivity.(Citation: FireEye TRITON Dec 2017) | relationship--5beda54d-cd1f-491b-a85e-d7618a0683ad | 28 March 2024 | 10 April 2024
C0030 | Triton Safety Instrumented System Attack | campaign--45a98f02-852f-49b2-94c0-c63207bebbbf | campaign | uses | T0843 | Program Download | attack-pattern--be69c571-d746-4b1f-bdd0-c0c9817e9068 | technique | In the [Triton Safety Instrumented System Attack](https://attack.mitre.org/campaigns/C0030), [TEMP.Veles](https://attack.mitre.org/groups/G0088) downloaded multiple rounds of control logic to the Safety Instrumented System (SIS) controllers through a program append operation.(Citation: FireEye TRITON Dec 2017) | relationship--81352e47-4317-45e3-88b9-a97dd2166727 | 28 March 2024 | 10 April 2024
C0030 | Triton Safety Instrumented System Attack | campaign--45a98f02-852f-49b2-94c0-c63207bebbbf | campaign | uses | T0886 | Remote Services | attack-pattern--e1f9cdd2-9511-4fca-90d7-f3e92cfdd0bf | technique | In the [Triton Safety Instrumented System Attack](https://attack.mitre.org/campaigns/C0030), [TEMP.Veles](https://attack.mitre.org/groups/G0088) utilized remote desktop protocol (RDP) jump boxes, poorly configured OT firewalls (Citation: Triton-EENews-2017), along with other traditional malware backdoors, to move into the ICS environment.(Citation: FireEye TRITON 2018)(Citation: Triton-EENews-2017) | relationship--cd6f1ca4-aaec-451d-b855-55cdb0c3dde8 | 28 March 2024 | 10 April 2024
C0030 | Triton Safety Instrumented System Attack | campaign--45a98f02-852f-49b2-94c0-c63207bebbbf | campaign | uses | T0853 | Scripting | attack-pattern--2dc2b567-8821-49f9-9045-8740f3d0b958 | technique | In the [Triton Safety Instrumented System Attack](https://attack.mitre.org/campaigns/C0030), [TEMP.Veles](https://attack.mitre.org/groups/G0088) used a publicly available PowerShell-based tool, WMImplant.(Citation: FireEye TEMP.Veles 2018) | relationship--3db8d8d2-89bb-4241-afeb-9b9332aac78e | 28 March 2024 | 10 April 2024
C0030 | Triton Safety Instrumented System Attack | campaign--45a98f02-852f-49b2-94c0-c63207bebbbf | campaign | uses | T0855 | Unauthorized Command Message | attack-pattern--40b300ba-f553-48bf-862e-9471b220d455 | technique | In the [Triton Safety Instrumented System Attack](https://attack.mitre.org/campaigns/C0030), [TEMP.Veles](https://attack.mitre.org/groups/G0088) leveraged [Triton](https://attack.mitre.org/software/S1009) to send unauthorized command messages to the Triconex safety controllers.(Citation: FireEye TRITON 2018) | relationship--fd7247a4-b299-4948-a3b0-9b43f4f41ae0 | 28 March 2024 | 10 April 2024
C0030 | Triton Safety Instrumented System Attack | campaign--45a98f02-852f-49b2-94c0-c63207bebbbf | campaign | uses | T0859 | Valid Accounts | attack-pattern--cd2c76a4-5e23-4ca5-9c40-d5e0604f7101 | technique | In the [Triton Safety Instrumented System Attack](https://attack.mitre.org/campaigns/C0030), [TEMP.Veles](https://attack.mitre.org/groups/G0088) used valid credentials when laterally moving through RDP jump boxes into the ICS environment.(Citation: FireEye TRITON 2018) | relationship--bf0e7347-1636-4b5e-9e2a-8b93177e5f85 | 28 March 2024 | 10 April 2024
C0031 | Unitronics Defacement Campaign | campaign--8fda050f-470d-4401-994e-35c1a6c301de | campaign | uses | T0812 | Default Credentials | attack-pattern--8bb4538f-f16f-49f0-a431-70b5444c7349 | technique | During the [Unitronics Defacement Campaign](https://attack.mitre.org/campaigns/C0031), the [CyberAv3ngers](https://attack.mitre.org/groups/G1027) discovered and exploited default credentials found on many Unitronics [Programmable Logic Controller (PLC)](https://attack.mitre.org/assets/A0003) [Human-Machine Interface (HMI)](https://attack.mitre.org/assets/A0002). For many of these devices, the default password was set to ‘1111’.(Citation: CISA AA23-335A IRGC-Affiliated December 2023)(Citation: CISA Unitronics November 2023) | relationship--1acc3a43-2961-4e4c-a237-f426a2df6be5 | 25 March 2024 | 15 April 2024
C0031 | Unitronics Defacement Campaign | campaign--8fda050f-470d-4401-994e-35c1a6c301de | campaign | uses | T0814 | Denial of Service | attack-pattern--1b22b676-9347-4c55-9a35-ef0dc653db5b | technique | During the [Unitronics Defacement Campaign](https://attack.mitre.org/campaigns/C0031), the [CyberAv3ngers](https://attack.mitre.org/groups/G1027) defaced controllers’ [Human-Machine Interface (HMI)](https://attack.mitre.org/assets/A0002), which prevented multiple entities from being able to operate their devices normally.(Citation: CISA AA23-335A IRGC-Affiliated December 2023)(Citation: CISA Unitronics November 2023)(Citation: Jamie Tarabay and Katrina Manson December 2023)(Citation: Frank Bajak and Marc Levy December 2023) Additionally, the [CyberAv3ngers](https://attack.mitre.org/groups/G1027) caused a communications failure in a remote pumping station.(Citation: WPXI Aliquippa Water November 2023) | relationship--18ab56e8-79ce-481d-9ab4-e558fbfb5ac5 | 25 March 2024 | 15 April 2024
C0031 | Unitronics Defacement Campaign | campaign--8fda050f-470d-4401-994e-35c1a6c301de | campaign | uses | T0883 | Internet Accessible Device | attack-pattern--f8df6b57-14bc-425f-9a91-6f59f6799307 | technique | During the [Unitronics Defacement Campaign](https://attack.mitre.org/campaigns/C0031), the [CyberAv3ngers](https://attack.mitre.org/groups/G1027) exploited devices connected to the public internet, such as internet connected Unitronics [Programmable Logic Controller (PLC)](https://attack.mitre.org/assets/A0003) with [Human-Machine Interface (HMI)](https://attack.mitre.org/assets/A0002) and networking equipment such as cellular modems found in OT environments.(Citation: CISA AA23-335A IRGC-Affiliated December 2023)(Citation: Lisa Zahner December 2023) | relationship--6b0e8f60-ecdf-4140-9741-5b50df67353c | 25 March 2024 | 15 April 2024
C0031 | Unitronics Defacement Campaign | campaign--8fda050f-470d-4401-994e-35c1a6c301de | campaign | uses | T0826 | Loss of Availability | attack-pattern--b5b9bacb-97f2-4249-b804-47fd44de1f95 | technique | During the [Unitronics Defacement Campaign](https://attack.mitre.org/campaigns/C0031), the [CyberAv3ngers](https://attack.mitre.org/groups/G1027) caused multiple businesses to halt operations due to the unavailability of the [Programmable Logic Controller (PLC)](https://attack.mitre.org/assets/A0003) and [Human-Machine Interface (HMI)](https://attack.mitre.org/assets/A0002). These victims covered multiple sectors.(Citation: Jamie Tarabay and Katrina Manson December 2023) | relationship--1673b2e2-7799-4b5f-b5a9-2c51426a6916 | 25 March 2024 | 15 April 2024
C0031 | Unitronics Defacement Campaign | campaign--8fda050f-470d-4401-994e-35c1a6c301de | campaign | uses | T0828 | Loss of Productivity and Revenue | attack-pattern--63b6942d-8359-4506-bfb3-cf87aa8120ee | technique | During the [Unitronics Defacement Campaign](https://attack.mitre.org/campaigns/C0031), the [CyberAv3ngers](https://attack.mitre.org/groups/G1027) caused multiple businesses to halt operations in their industrial environments, impacting their typical business operations. These victims covered multiple sectors.(Citation: Jamie Tarabay and Katrina Manson December 2023) | relationship--d67ae959-9014-4501-b963-42bee03a5e3b | 25 March 2024 | 15 April 2024
C0031 | Unitronics Defacement Campaign | campaign--8fda050f-470d-4401-994e-35c1a6c301de | campaign | uses | T0829 | Loss of View | attack-pattern--138979ba-0430-4de6-a128-2fc0b056ba36 | technique | During the [Unitronics Defacement Campaign](https://attack.mitre.org/campaigns/C0031), the [CyberAv3ngers](https://attack.mitre.org/groups/G1027) replaced the existing graphic on the [Programmable Logic Controller (PLC)](https://attack.mitre.org/assets/A0003) [Human-Machine Interface (HMI)](https://attack.mitre.org/assets/A0002) with their own, thereby preventing PLC owners and operators from viewing PLC information on the HMI.(Citation: CISA AA23-335A IRGC-Affiliated December 2023)(Citation: Jamie Tarabay and Katrina Manson December 2023) | relationship--69889c90-e6d0-4007-9078-2bfbd7c18a91 | 25 March 2024 | 15 April 2024
G1000 | ALLANITE | intrusion-set--190242d7-73fc-4738-af68-20162f7a5aae | group | uses | T0817 | Drive-by Compromise | attack-pattern--7830cfcf-b268-4ac0-a69e-73c6affbae9a | technique | [ALLANITE](https://attack.mitre.org/groups/G1000) leverages watering hole attacks to gain access into electric utilities. (Citation: Eduard Kovacs May 2018) | relationship--fc4803cb-d6bf-4674-bf40-d4b0997824ba | 18 April 2018 | 12 September 2024
G1000 | ALLANITE | intrusion-set--190242d7-73fc-4738-af68-20162f7a5aae | group | uses | T0852 | Screen Capture | attack-pattern--c5e3cdbc-0387-4be9-8f83-ff5c0865f377 | technique | [ALLANITE](https://attack.mitre.org/groups/G1000) has been identified to collect and distribute screenshots of ICS systems such as HMIs. (Citation: Dragos) (Citation: ICS-CERT October 2017) | relationship--5424e327-396f-4b07-94a3-408ffc915686 | 18 April 2018 | 12 October 2022
G1000 | ALLANITE | intrusion-set--190242d7-73fc-4738-af68-20162f7a5aae | group | uses | T0865 | Spearphishing Attachment | attack-pattern--648f995e-9c3a-41e4-aeee-98bb41037426 | technique | [ALLANITE](https://attack.mitre.org/groups/G1000) utilized spear phishing to gain access into energy sector environments. (Citation: Jeff Jones May 2018) | relationship--679e7b8d-57d7-4c1d-8f42-1496606ea666 | 18 April 2018 | 12 October 2022
G1000 | ALLANITE | intrusion-set--190242d7-73fc-4738-af68-20162f7a5aae | group | uses | T0859 | Valid Accounts | attack-pattern--cd2c76a4-5e23-4ca5-9c40-d5e0604f7101 | technique | [ALLANITE](https://attack.mitre.org/groups/G1000) utilized credentials collected through phishing and watering hole attacks. (Citation: Dragos) | relationship--0eb112f6-c1cb-4843-93f5-f668aa0e9bd8 | 18 April 2018 | 12 October 2022
G0064 | APT33 | intrusion-set--fbd29c89-18ba-4c2d-b792-51c0adee049f | group | uses | T0852 | Screen Capture | attack-pattern--c5e3cdbc-0387-4be9-8f83-ff5c0865f377 | technique | [APT33](https://attack.mitre.org/groups/G0064) utilize backdoors capable of capturing screenshots once installed on a system. (Citation: Jacqueline O'Leary et al. September 2017)(Citation: Junnosuke Yagi March 2017) | relationship--0beb0088-3bea-4612-b2d9-ff9988f829ae | 18 April 2018 | 12 October 2022
G0064 | APT33 | intrusion-set--fbd29c89-18ba-4c2d-b792-51c0adee049f | group | uses | T0853 | Scripting | attack-pattern--2dc2b567-8821-49f9-9045-8740f3d0b958 | technique | [APT33](https://attack.mitre.org/groups/G0064) utilized PowerShell scripts to establish command and control and install files for execution. (Citation: Symantec March 2019) (Citation: Dragos) | relationship--739e7b8d-57d7-4c1d-8f42-1496606ea666 | 18 April 2018 | 12 October 2022
G0064 | APT33 | intrusion-set--fbd29c89-18ba-4c2d-b792-51c0adee049f | group | uses | T0865 | Spearphishing Attachment | attack-pattern--648f995e-9c3a-41e4-aeee-98bb41037426 | technique | [APT33](https://attack.mitre.org/groups/G0064) sent spear phishing emails containing links to HTML application files, which were embedded with malicious code. (Citation: Jacqueline O'Leary et al. September 2017) [APT33](https://attack.mitre.org/groups/G0064) has conducted targeted spear phishing campaigns against U.S. government agencies and private sector companies. (Citation: Andy Greenburg June 2019) | relationship--0f18b876-b698-4f70-aa98-50e8b5a7eae2 | 18 April 2018 | 12 October 2022
G0035 | Dragonfly | intrusion-set--1c63d4ec-0a75-4daa-b1df-0d11af3d3cc1 | group | uses | T0817 | Drive-by Compromise | attack-pattern--7830cfcf-b268-4ac0-a69e-73c6affbae9a | technique | [Dragonfly](https://attack.mitre.org/groups/G0035) utilized watering hole attacks on energy sector websites by injecting a redirect iframe to deliver [Backdoor.Oldrea](https://attack.mitre.org/software/S0093) or [Trojan.Karagany](https://attack.mitre.org/software/S0094). (Citation: Symantec Security Response July 2014) | relationship--042243fd-bfe0-4961-96de-a36232d3ff74 | 18 April 2018 | 12 October 2022
G0035 | Dragonfly | intrusion-set--1c63d4ec-0a75-4daa-b1df-0d11af3d3cc1 | group | uses | T0862 | Supply Chain Compromise | attack-pattern--5e0f75da-e108-4688-a6de-a4f07cc2cbe3 | technique | [Dragonfly](https://attack.mitre.org/groups/G0035) trojanized legitimate ICS equipment providers software packages available for download on their websites.(Citation: Symantec Security Response July 2014) | relationship--ef615d62-fe85-4740-9c5d-5dddff9b5693 | 18 April 2018 | 12 October 2022
G0032 | Lazarus Group | intrusion-set--c93fccb1-e8e8-42cf-ae33-2ad1d183913a | group | uses | T0865 | Spearphishing Attachment | attack-pattern--648f995e-9c3a-41e4-aeee-98bb41037426 | technique | [Lazarus Group](https://attack.mitre.org/groups/G0032) has been observed targeting organizations using spearphishing documents with embedded malicious payloads. (Citation: Novetta Threat Research Group February 2016) Highly targeted spear phishing campaigns have been conducted against a U.S. electric grid company. (Citation: Eduard Kovacs March 2018) | relationship--31bf1721-78a2-4b6c-b325-5c44dc02ea33 | 14 December 2017 | 04 October 2024
G0049 | OilRig | intrusion-set--4ca1929c-7d64-4aab-b849-badbfc0c760d | group | uses | T0817 | Drive-by Compromise | attack-pattern--7830cfcf-b268-4ac0-a69e-73c6affbae9a | technique | [OilRig](https://attack.mitre.org/groups/G0049) has been seen utilizing watering hole attacks to collect credentials which could be used to gain access into ICS networks. (Citation: Eduard Kovacs May 2018) | relationship--f8318ac4-8ed0-478d-be87-faa2c9d8a740 | 17 October 2018 | 12 September 2024
G0049 | OilRig | intrusion-set--4ca1929c-7d64-4aab-b849-badbfc0c760d | group | uses | T0853 | Scripting | attack-pattern--2dc2b567-8821-49f9-9045-8740f3d0b958 | technique | [OilRig](https://attack.mitre.org/groups/G0049) has embedded a macro within spearphishing attachments that has been made up of both a VBScript and a PowerShell script.(Citation: Robert Falcone, Bryan Lee May 2016) | relationship--c4e8dd42-9855-4a36-b915-dc7e1a91e235 | 17 October 2018 | 12 October 2022
G0049 | OilRig | intrusion-set--4ca1929c-7d64-4aab-b849-badbfc0c760d | group | uses | T0865 | Spearphishing Attachment | attack-pattern--648f995e-9c3a-41e4-aeee-98bb41037426 | technique | [OilRig](https://attack.mitre.org/groups/G0049) used spearphishing emails with malicious Microsoft Excel spreadsheet attachments. (Citation: Robert Falcone, Bryan Lee May 2016) | relationship--3618a010-b94b-4974-b1be-7630d5c853c1 | 17 October 2018 | 12 October 2022
G0049 | OilRig | intrusion-set--4ca1929c-7d64-4aab-b849-badbfc0c760d | group | uses | T0869 | Standard Application Layer Protocol | attack-pattern--e076cca8-2f08-45c9-aff7-ea5ac798b387 | technique | [OilRig](https://attack.mitre.org/groups/G0049) communicated with its command and control using HTTP requests. (Citation: Robert Falcone, Bryan Lee May 2016) | relationship--d2dc57eb-5be2-4f9c-a4f7-18d2085ff412 | 17 October 2018 | 12 October 2022
G0049 | OilRig | intrusion-set--4ca1929c-7d64-4aab-b849-badbfc0c760d | group | uses | T0859 | Valid Accounts | attack-pattern--cd2c76a4-5e23-4ca5-9c40-d5e0604f7101 | technique | [OilRig](https://attack.mitre.org/groups/G0049) utilized stolen credentials to gain access to victim machines.(Citation: Dragos) | relationship--f65a8ce8-90fa-4d92-a0dc-3ee544c541fe | 17 October 2018 | 12 October 2022
G0034 | Sandworm Team | intrusion-set--381fcf73-60f6-4ab2-9991-6af3cbc35192 | group | uses | T0807 | Command-Line Interface | attack-pattern--24a9253e-8948-4c98-b751-8e2aee53127c | technique | [Sandworm Team](https://attack.mitre.org/groups/G0034) uses the MS-SQL server xp_cmdshell command, and PowerShell to execute commands. (Citation: Dragos October 2018) | relationship--26d68f5d-6ee5-4d98-b175-943366ccc038 | 14 October 2020 | 12 October 2022
G0034 | Sandworm Team | intrusion-set--381fcf73-60f6-4ab2-9991-6af3cbc35192 | group | uses | T0884 | Connection Proxy | attack-pattern--d67adac8-e3b9-44f9-9e6d-6c2a7d69dbe4 | technique | [Sandworm Team](https://attack.mitre.org/groups/G0034) establishes an internal proxy prior to the installation of backdoors within the network. (Citation: Dragos Inc. June 2017) | relationship--eb1e05ef-58df-4c6d-acd7-5cc63ff7f44f | 08 October 2021 | 12 October 2022
G0034 | Sandworm Team | intrusion-set--381fcf73-60f6-4ab2-9991-6af3cbc35192 | group | uses | T0819 | Exploit Public-Facing Application | attack-pattern--32632a95-6856-47b9-9ab7-fea5cd7dce00 | technique | [Sandworm Team](https://attack.mitre.org/groups/G0034) actors exploited vulnerabilities in GE's Cimplicity HMI and Advantech/Broadwin WebAccess HMI software which had been directly exposed to the internet. (Citation: ICS-CERT December 2014) (Citation: ICS CERT September 2018) | relationship--a846dbe5-9ef3-4fb6-93d5-f764671a75c8 | 11 April 2021 | 12 October 2022
G0088 | TEMP.Veles | intrusion-set--9538b1a4-4120-4e2d-bf59-3b11fcab05a4 | group | uses | T0817 | Drive-by Compromise | attack-pattern--7830cfcf-b268-4ac0-a69e-73c6affbae9a | technique | [TEMP.Veles](https://attack.mitre.org/groups/G0088) utilizes watering hole websites to target industrial employees. (Citation: Chris Bing May 2018) | relationship--b3862aa6-7bd0-46a4-83b6-bb687bb7caa6 | 17 October 2018 | 12 October 2022
G0088 | TEMP.Veles | intrusion-set--9538b1a4-4120-4e2d-bf59-3b11fcab05a4 | group | uses | T0862 | Supply Chain Compromise | attack-pattern--5e0f75da-e108-4688-a6de-a4f07cc2cbe3 | technique | [TEMP.Veles](https://attack.mitre.org/groups/G0088) targeted several ICS vendors and manufacturers. (Citation: Dragos Threat Intelligence August 2019) | relationship--b343e131-e448-46c6-815b-b86e4bd6d638 | 17 October 2018 | 12 October 2022
S1000 | ACAD/Medre.A | malware--a4a98eab-b691-45d9-8c48-869ef8fefd57 | software | uses | T0893 | Data from Local System | attack-pattern--fa3aa267-da22-4bdd-961f-03223322a8d5 | technique | [ACAD/Medre.A](https://attack.mitre.org/software/S1000) collects information related to the AutoCAD application. The worm collects AutoCAD (*.dwg) files with drawings from infected systems. (Citation: ESET) | relationship--274994e7-1fe9-463a-9979-46c72107bf9b | 30 March 2023 | 30 March 2023
S1000 | ACAD/Medre.A | malware--a4a98eab-b691-45d9-8c48-869ef8fefd57 | software | uses | T0882 | Theft of Operational Information | attack-pattern--b7e13ee8-182c-4f19-92a4-a88d7d855d54 | technique | [ACAD/Medre.A](https://attack.mitre.org/software/S1000) can collect AutoCad files with drawings. These drawings may contain operational information. (Citation: ESET) | relationship--228b9a13-0545-4ecf-99ff-be02addaf7fe | 17 October 2018 | 12 October 2022
S0093 | Backdoor.Oldrea | malware--083bb47b-02c8-4423-81a2-f9ef58572974 | software | uses | T0802 | Automated Collection | attack-pattern--3de230d4-3e42-4041-b089-17e1128feded | technique | Using OPC, a component of [Backdoor.Oldrea](https://attack.mitre.org/software/S0093) gathers any details about connected devices and sends them back to the C2 for the attackers to analyze. (Citation: Daavid Hentunen, Antti Tikkanen June 2014) | relationship--8f76d408-be8a-478e-8a5a-aab1d1f96572 | 18 April 2018 | 12 October 2022
S0093 | Backdoor.Oldrea | malware--083bb47b-02c8-4423-81a2-f9ef58572974 | software | uses | T0814 | Denial of Service | attack-pattern--1b22b676-9347-4c55-9a35-ef0dc653db5b | technique | The [Backdoor.Oldrea](https://attack.mitre.org/software/S0093) payload has caused multiple common OPC platforms to intermittently crash. This could cause a denial of service effect on applications reliant on OPC communications. (Citation: ICS-CERT August 2018) | relationship--d90aeeb6-3686-483a-8403-6514ecfe1a50 | 18 April 2018 | 12 October 2022
S0093 | Backdoor.Oldrea | malware--083bb47b-02c8-4423-81a2-f9ef58572974 | software | uses | T0861 | Point & Tag Identification | attack-pattern--25852363-5968-4673-b81d-341d5ed90bd1 | technique | The [Backdoor.Oldrea](https://attack.mitre.org/software/S0093) payload has the capability of enumerating OPC tags, in addition to more generic OPC server information. The server data and tag names can provide information about the names and function of control devices. (Citation: ICS-CERT August 2018) (Citation: Daavid Hentunen, Antti Tikkanen June 2014) | relationship--90d9c8e3-0250-4096-8d98-7ca1d324d654 | 12 April 2021 | 12 October 2022
S0093 | Backdoor.Oldrea | malware--083bb47b-02c8-4423-81a2-f9ef58572974 | software | uses | T0846 | Remote System Discovery | attack-pattern--d5a69cfb-fc2a-46cb-99eb-74b236db5061 | technique | The [Backdoor.Oldrea](https://attack.mitre.org/software/S0093) ICS malware plugin relies on Windows networking (WNet) to discover all the servers, including OPC servers, that are reachable by the compromised machine over the network. (Citation: Julian Rrushi, Hassan Farhangi, Clay Howey, Kelly Carmichael, Joey Dabell December 2015) | relationship--3f76d408-be8a-478e-8a5a-aab1d1f96572 | 18 April 2018 | 11 August 2022
S0093 | Backdoor.Oldrea | malware--083bb47b-02c8-4423-81a2-f9ef58572974 | software | uses | T0888 | Remote System Information Discovery | attack-pattern--2fedbe69-581f-447d-8a78-32ee7db939a9 | technique | The [Backdoor.Oldrea](https://attack.mitre.org/software/S0093) payload gathers server information that includes CLSID, server name, Program ID, OPC version, vendor information, running state, group count, and server bandwidth. This information helps indicate the role the server has in the control process. (Citation: ICS-CERT August 2018) (Citation: Daavid Hentunen, Antti Tikkanen June 2014) | relationship--067932c3-0011-4ca2-9bbe-721c631e4e41 | 13 April 2021 | 12 October 2022
S0093 | Backdoor.Oldrea | malware--083bb47b-02c8-4423-81a2-f9ef58572974 | software | uses | T0865 | Spearphishing Attachment | attack-pattern--648f995e-9c3a-41e4-aeee-98bb41037426 | technique | The [Backdoor.Oldrea](https://attack.mitre.org/software/S0093) RAT is distributed through a trojanized installer attached to emails. (Citation: Daavid Hentunen, Antti Tikkanen June 2014) | relationship--e0aee02c-b424-4781-be10-793d71594c31 | 18 April 2018 | 12 October 2022
S0093 | Backdoor.Oldrea | malware--083bb47b-02c8-4423-81a2-f9ef58572974 | software | uses | T0862 | Supply Chain Compromise | attack-pattern--5e0f75da-e108-4688-a6de-a4f07cc2cbe3 | technique | The [Backdoor.Oldrea](https://attack.mitre.org/software/S0093) RAT is distributed through trojanized installers planted on compromised vendor sites. (Citation: Daavid Hentunen, Antti Tikkanen June 2014) | relationship--6d822f86-5793-403a-b176-5d533f6b81b3 | 18 April 2018 | 12 October 2022
S0093 | Backdoor.Oldrea | malware--083bb47b-02c8-4423-81a2-f9ef58572974 | software | uses | T0863 | User Execution | attack-pattern--2736b752-4ec5-4421-a230-8977dea7649c | technique | Execution of [Backdoor.Oldrea](https://attack.mitre.org/software/S0093) relies on a user opening a trojanized installer attached to an email. (Citation: Daavid Hentunen, Antti Tikkanen June 2014) (Citation: Kyle Wilhoit) | relationship--5bb313a8-8407-4ec1-a4b0-683ded7f3302 | 18 April 2018 | 12 October 2022
S0606 | Bad Rabbit | malware--2eaa5319-5e1e-4dd7-bbc4-566fced3964a | software | uses | T0817 | Drive-by Compromise | attack-pattern--7830cfcf-b268-4ac0-a69e-73c6affbae9a | technique | [Bad Rabbit](https://attack.mitre.org/software/S0606) ransomware spreads through drive-by attacks where insecure websites are compromised. While the target is visiting a legitimate website, a malware dropper is being downloaded from the threat actors infrastructure. (Citation: Orkhan Mamedov, Fedor Sinitsyn, Anton Ivanov October 2017) | relationship--0c1fe5fc-3bdc-4d0e-94a0-6564f2ce4444 | 31 May 2017 | 12 October 2022
S0606 | Bad Rabbit | malware--2eaa5319-5e1e-4dd7-bbc4-566fced3964a | software | uses | T0866 | Exploitation of Remote Services | attack-pattern--85a45294-08f1-4539-bf00-7da08aa7b0ee | technique | [Bad Rabbit](https://attack.mitre.org/software/S0606) initially infected IT networks, but by means of an exploit (particularly the SMBv1-targeting MS17-010 vulnerability) spread to industrial networks. (Citation: Joe Slowik April 2019) | relationship--058396ca-3af4-444b-b261-74485c47e68c | 31 May 2017 | 12 October 2022
S0606 | Bad Rabbit | malware--2eaa5319-5e1e-4dd7-bbc4-566fced3964a | software | uses | T0867 | Lateral Tool Transfer | attack-pattern--ead7bd34-186e-4c79-9a4d-b65bcce6ed9d | technique | [Bad Rabbit](https://attack.mitre.org/software/S0606) can move laterally through industrial networks by means of the SMB service. (Citation: Joe Slowik April 2019) | relationship--ffc5bbce-8d9c-4276-9dc6-efed5c01af8b | 31 May 2017 | 12 October 2022
S0606 | Bad Rabbit | malware--2eaa5319-5e1e-4dd7-bbc4-566fced3964a | software | uses | T0828 | Loss of Productivity and Revenue | attack-pattern--63b6942d-8359-4506-bfb3-cf87aa8120ee | technique | Several transportation organizations in Ukraine have suffered from being infected by [Bad Rabbit](https://attack.mitre.org/software/S0606), resulting in some computers becoming encrypted, according to media reports. (Citation: Marc-Etienne M.Lveill October 2017) | relationship--d7ea83fa-87c7-4d36-96d5-aee554504040 | 31 May 2017 | 12 October 2022
S0606 | Bad Rabbit | malware--2eaa5319-5e1e-4dd7-bbc4-566fced3964a | software | uses | T0863 | User Execution | attack-pattern--2736b752-4ec5-4421-a230-8977dea7649c | technique | [Bad Rabbit](https://attack.mitre.org/software/S0606) is disguised as an Adobe Flash installer. When the file is opened it starts locking the infected computer. (Citation: Orkhan Mamedov, Fedor Sinitsyn, Anton Ivanov October 2017) | relationship--edf73653-b2d7-422f-b433-b6a428ff12d4 | 31 May 2017 | 12 October 2022
S0089 | BlackEnergy | malware--54cc1d4f-5c53-4f0e-9ef5-11b4998e82e4 | software | uses | T0865 | Spearphishing Attachment | attack-pattern--648f995e-9c3a-41e4-aeee-98bb41037426 | technique | [BlackEnergy](https://attack.mitre.org/software/S0089) targeted energy sector organizations in a wide reaching email spearphishing campaign. Adversaries utilized malicious Microsoft Word documents attachments. (Citation: Booz Allen Hamilton) | relationship--d9165ecb-bc10-4189-a7e4-057bdf05bf3f | 14 December 2017 | 12 October 2022
S0089 | BlackEnergy | malware--54cc1d4f-5c53-4f0e-9ef5-11b4998e82e4 | software | uses | T0869 | Standard Application Layer Protocol | attack-pattern--e076cca8-2f08-45c9-aff7-ea5ac798b387 | technique | [BlackEnergy](https://attack.mitre.org/software/S0089) uses HTTP POST request to contact external command and control servers. (Citation: Booz Allen Hamilton) | relationship--3a7d1db3-9383-4171-8938-382e9b0375c6 | 14 December 2017 | 12 October 2022
S0089 | BlackEnergy | malware--54cc1d4f-5c53-4f0e-9ef5-11b4998e82e4 | software | uses | T0859 | Valid Accounts | attack-pattern--cd2c76a4-5e23-4ca5-9c40-d5e0604f7101 | technique | [BlackEnergy](https://attack.mitre.org/software/S0089) utilizes valid user and administrator credentials, in addition to creating new administrator accounts to maintain presence. (Citation: Booz Allen Hamilton) | relationship--ee2fdebd-1587-4e53-a7d7-c15fcc88879d | 14 December 2017 | 12 October 2022
S0608 | Conficker | malware--58eddbaf-7416-419a-ad7b-e65b9d4c3b55 | software | uses | T0826 | Loss of Availability | attack-pattern--b5b9bacb-97f2-4249-b804-47fd44de1f95 | technique | A [Conficker](https://attack.mitre.org/software/S0608) infection at a nuclear power plant forced the facility to temporarily shutdown. (Citation: Catalin Cimpanu April 2016) | relationship--990f944f-190d-456d-b194-f5ecb17a0868 | 24 June 2019 | 12 October 2022
S0608 | Conficker | malware--58eddbaf-7416-419a-ad7b-e65b9d4c3b55 | software | uses | T0828 | Loss of Productivity and Revenue | attack-pattern--63b6942d-8359-4506-bfb3-cf87aa8120ee | technique | A [Conficker](https://attack.mitre.org/software/S0608) infection at a nuclear power plant forced the facility to shutdown and go through security procedures involved with such events, with its staff scanning computer systems and going through all the regular checks and motions before putting the plant back into production. (Citation: Catalin Cimpanu April 2016) | relationship--51f9963c-c041-4bec-b482-5fda2fb5bca4 | 24 June 2019 | 12 October 2022
S0608 | Conficker | malware--58eddbaf-7416-419a-ad7b-e65b9d4c3b55 | software | uses | T0847 | Replication Through Removable Media | attack-pattern--c267bbee-bb59-47fe-85e0-3ed210337c21 | technique | [Conficker](https://attack.mitre.org/software/S0608) exploits Windows drive shares. Once it has infected a computer, [Conficker](https://attack.mitre.org/software/S0608) automatically copies itself to all visible open drive shares on other computers inside the network. (Citation: Symantec June 2015) Nuclear power plant officials suspect someone brought in [Conficker](https://attack.mitre.org/software/S0608) by accident on a USB thumb drive, either from home or computers found in the power plant's facility. (Citation: Catalin Cimpanu April 2016) | relationship--71422483-33e4-4131-a4ec-40322d91d8a0 | 24 June 2019 | 17 October 2022
S0038 | Duqu | malware--68dca94f-c11d-421e-9287-7c501108e18c | software | uses | T0811 | Data from Information Repositories | attack-pattern--3405891b-16aa-4bd7-bd7c-733501f9b20f | technique | [Duqu](https://attack.mitre.org/software/S0038) downloads additional modules for the collection of data in information repositories, including the Infostealer 2 module that can access data from Windows Shares.(Citation: Symantec) | relationship--692324b4-064a-430c-8ffc-7f7acd537778 | 17 October 2018 | 30 March 2023
S0038 | Duqu | malware--68dca94f-c11d-421e-9287-7c501108e18c | software | uses | T0893 | Data from Local System | attack-pattern--fa3aa267-da22-4bdd-961f-03223322a8d5 | technique | [Duqu](https://attack.mitre.org/software/S0038) downloads additional modules for the collection of data from local systems. The modules are named: infostealer 1, infostealer 2 and reconnaissance. (Citation: Symantec) | relationship--172e0537-7a9c-4610-9b07-32a841f0bd8d | 30 March 2023 | 30 March 2023
S0038 | Duqu | malware--68dca94f-c11d-421e-9287-7c501108e18c | software | uses | T0882 | Theft of Operational Information | attack-pattern--b7e13ee8-182c-4f19-92a4-a88d7d855d54 | technique | [Duqu](https://attack.mitre.org/software/S0038)'s purpose is to gather intelligence data and assets from entities such as industrial infrastructure and system manufacturers, amongst others not in the industrial sector, in order to more easily conduct a future attack against another third party.(Citation: Symantec) | relationship--792324b4-064a-430c-8ffc-7f7acd537778 | 17 October 2018 | 12 October 2022
S0605 | EKANS | malware--00e7d565-9883-4ee5-b642-8fd17fd6a3f5 | software | uses | T0828 | Loss of Productivity and Revenue | attack-pattern--63b6942d-8359-4506-bfb3-cf87aa8120ee | technique | [EKANS](https://attack.mitre.org/software/S0605) infection resulted in a temporary production loss within a Honda manufacturing plant. (Citation: Davey Winder June 2020) | relationship--a6519c11-e9d4-4b6f-8d92-8efaa2144c28 | 13 April 2021 | 12 October 2022
S0605 | EKANS | malware--00e7d565-9883-4ee5-b642-8fd17fd6a3f5 | software | uses | T0849 | Masquerading | attack-pattern--ba203963-3182-41ac-af14-7e7ebc83cd61 | technique | [EKANS](https://attack.mitre.org/software/S0605) masquerades itself as a valid executable with the filename update.exe. Many valid programs use the process name update.exe to perform background software updates. (Citation: Dragos Threat Intelligence February 2020) | relationship--c347b69c-e3f6-4eca-ba57-0781c7dc8eac | 13 April 2021 | 12 October 2022
S0605 | EKANS | malware--00e7d565-9883-4ee5-b642-8fd17fd6a3f5 | software | uses | T0840 | Network Connection Enumeration | attack-pattern--ea0c980c-5cf0-43a7-a049-59c4c207566e | technique | [EKANS](https://attack.mitre.org/software/S0605) performs a DNS lookup of an internal domain name associated with its target network to identify if it was deployed on the intended system. (Citation: Ben Hunter and Fred Gutierrez July 2020) | relationship--1dc35f79-0ada-4342-bd13-10d10c1b0335 | 13 April 2021 | 12 October 2022
S0605 | EKANS | malware--00e7d565-9883-4ee5-b642-8fd17fd6a3f5 | software | uses | T0881 | Service Stop | attack-pattern--063b5b92-5361-481a-9c3f-95492ed9a2d8 | technique | Before encrypting the process, [EKANS](https://attack.mitre.org/software/S0605) first kills the process if its name matches one of the processes defined on the kill-list. (Citation: Daniel Kapellmann Zafra, Keith Lunden, Nathan Brubaker, Jeremy Kennelly July 2020) (Citation: Daniel Kapellmann Zafra, Keith Lunden, Nathan Brubaker, Jeremy Kennelly July 2020) EKANS also utilizes netsh commands to implement firewall rules that blocks any remote communication with the device. (Citation: Ben Hunter and Fred Gutierrez July 2020) | relationship--11e4eb54-b0b3-4f67-a93f-28cc10df00ab | 13 April 2021 | 12 October 2022
S0143 | Flame | malware--ff6840c9-4c87-4d07-bbb6-9f50aa33d498 | software | uses | T0893 | Data from Local System | attack-pattern--fa3aa267-da22-4bdd-961f-03223322a8d5 | technique | [Flame](https://attack.mitre.org/software/S0143) has built-in modules to gather information from compromised computers. (Citation: Kevin Savage and Branko Spasojevic) | relationship--25ddb2e0-b945-45d2-a8a9-6e6d5c4401d3 | 30 March 2023 | 30 March 2023
S0143 | Flame | malware--ff6840c9-4c87-4d07-bbb6-9f50aa33d498 | software | uses | T0882 | Theft of Operational Information | attack-pattern--b7e13ee8-182c-4f19-92a4-a88d7d855d54 | technique | [Flame](https://attack.mitre.org/software/S0143) can collect AutoCAD design data and visio diagrams as well as other documents that may contain operational information. (Citation: Kevin Savage and Branko Spasojevic) | relationship--79d05cb2-ded0-4847-b52e-af7af421f303 | 14 December 2017 | 12 October 2022
S1157 | Fuxnet | malware--931e2489-8078-4f9f-85b2-a9211950e75b | software | uses | T0806 | Brute Force I/O | attack-pattern--8e7089d3-fba2-44f8-94a8-9a79c53920c4 | technique | [Fuxnet](https://attack.mitre.org/software/S1157) repeatedly wrote arbitrary data over the Meter-Bus channel from impacted devices to connected sensors to render sensor data acquisition useless.(Citation: Claroty Fuxnet 2024) | relationship--6f9e3f69-ac1c-479e-ae2d-73dd1413d4dd | 11 September 2024 | 11 September 2024
S1157 | Fuxnet | malware--931e2489-8078-4f9f-85b2-a9211950e75b | software | uses | T0809 | Data Destruction | attack-pattern--493832d9-cea6-4b63-abe7-9a65a6473675 | technique | [Fuxnet](https://attack.mitre.org/software/S1157) physically destroyed NAND memory chips on impacted devices through repeated bit-flip operations.(Citation: Claroty Fuxnet 2024) | relationship--faf163b6-4e35-43d6-9c0c-83d91d215854 | 11 September 2024 | 11 September 2024
S1157 | Fuxnet | malware--931e2489-8078-4f9f-85b2-a9211950e75b | software | uses | T0814 | Denial of Service | attack-pattern--1b22b676-9347-4c55-9a35-ef0dc653db5b | technique | [Fuxnet](https://attack.mitre.org/software/S1157) shut down remote access services such as SSH, HTTP, telnet, and SNMP to a device along with deleting the routing table for routing devices to inhibit system accessibility and communication.(Citation: Claroty Fuxnet 2024) | relationship--a6277ff6-9cdf-484f-a902-3f9442039905 | 11 September 2024 | 11 September 2024
S1157 | Fuxnet | malware--931e2489-8078-4f9f-85b2-a9211950e75b | software | uses | T0822 | External Remote Services | attack-pattern--8d2f3bab-507c-4424-b58b-edc977bd215c | technique | [Fuxnet](https://attack.mitre.org/software/S1157) initial execution relied on accessing external remote services for victim environments.(Citation: Claroty Fuxnet 2024) | relationship--66eb9d6f-498b-4a9a-94d3-fe808460bb68 | 11 September 2024 | 11 September 2024
S1157 | Fuxnet | malware--931e2489-8078-4f9f-85b2-a9211950e75b | software | uses | T0883 | Internet Accessible Device | attack-pattern--f8df6b57-14bc-425f-9a91-6f59f6799307 | technique | [Fuxnet](https://attack.mitre.org/software/S1157) execution relied upon accessing Internet-accessible devices for initial access and deployment.(Citation: Claroty Fuxnet 2024) | relationship--1b36c370-6e82-4c2f-936d-a6fe8aafc73d | 11 September 2024 | 11 September 2024
S1157 | Fuxnet | malware--931e2489-8078-4f9f-85b2-a9211950e75b | software | uses | T0829 | Loss of View | attack-pattern--138979ba-0430-4de6-a128-2fc0b056ba36 | technique | [Fuxnet](https://attack.mitre.org/software/S1157) impaired sensor communication to impacted devices resulting in a loss of view condition for overall system monitoring.(Citation: Claroty Fuxnet 2024) | relationship--7200f777-0ddd-4c9c-a022-26d49ea524d3 | 11 September 2024 | 11 September 2024
S1045 | INCONTROLLER | malware--d3aa1058-b1b3-4c29-a3ba-9a9b90ccd93b | software | uses | T0858 | Change Operating Mode | attack-pattern--2883c520-7957-46ca-89bd-dab1ad53b601 | technique | [INCONTROLLER](https://attack.mitre.org/software/S1045) can establish a remote HTTP connection to change the operating mode of Omron PLCs.(Citation: Dragos-Pipedream)(Citation: Wylie-22) | relationship--51eb15a3-48af-470f-94c0-10f25b366d72 | 28 September 2022 | 13 October 2022
S1045 | INCONTROLLER | malware--d3aa1058-b1b3-4c29-a3ba-9a9b90ccd93b | software | uses | T0884 | Connection Proxy | attack-pattern--d67adac8-e3b9-44f9-9e6d-6c2a7d69dbe4 | technique | The [INCONTROLLER](https://attack.mitre.org/software/S1045) PLCProxy module can add an IP route to the CODESYS gateway running on Schneider PLCs to allow it to route messages through the PLC to other devices on that network. This allows the malware to bypass firewall rules that prevent it from directly communicating with devices on the same network as the PLC.(Citation: Wylie-22) | relationship--40479f3e-d4d2-45f8-893f-f8a4fcf1613c | 28 September 2022 | 13 October 2022
S1045 | INCONTROLLER | malware--d3aa1058-b1b3-4c29-a3ba-9a9b90ccd93b | software | uses | T0809 | Data Destruction | attack-pattern--493832d9-cea6-4b63-abe7-9a65a6473675 | technique | [INCONTROLLER](https://attack.mitre.org/software/S1045) can wipe the memory of Omron PLCs and reset settings through the remote HTTP service.(Citation: Brubaker-Incontroller)(Citation: Dragos-Pipedream)(Citation: Wylie-22) | relationship--e3923fcf-5580-4c1e-bc55-33f67792cc00 | 28 September 2022 | 13 October 2022
S1045 | INCONTROLLER | malware--d3aa1058-b1b3-4c29-a3ba-9a9b90ccd93b | software | uses | T0890 | Exploitation for Privilege Escalation | attack-pattern--cfe68e93-ce94-4c0f-a57d-3aa72cedd618 | technique | [INCONTROLLER](https://attack.mitre.org/software/S1045) has the ability to exploit a vulnerable Asrock driver (AsrDrv103.sys) using CVE-2020-15368 to load its own unsigned driver on the system.(Citation: Wylie-22) | relationship--cba8313b-c338-45f7-88ef-a514094882ac | 28 September 2022 | 13 October 2022
S1045 | INCONTROLLER | malware--d3aa1058-b1b3-4c29-a3ba-9a9b90ccd93b | software | uses | T0891 | Hardcoded Credentials | attack-pattern--c9a8d958-fcdb-40d2-af4c-461c8031651a | technique | [INCONTROLLER](https://attack.mitre.org/software/S1045) can login to Omron PLCs using hardcoded credentials, which is documented in CVE-2022-34151.(Citation: Wylie-22) | relationship--1f785984-791e-4612-be32-9ee6903a9c0b | 28 September 2022 | 13 October 2022
S1045 | INCONTROLLER | malware--d3aa1058-b1b3-4c29-a3ba-9a9b90ccd93b | software | uses | T0867 | Lateral Tool Transfer | attack-pattern--ead7bd34-186e-4c79-9a4d-b65bcce6ed9d | technique | [INCONTROLLER](https://attack.mitre.org/software/S1045) can use a Telnet session to load a malware implant on Omron PLCs.(Citation: CISA-AA22-103A)(Citation: Wylie-22) | relationship--868db512-b897-4a54-ae56-ac78f6c93a14 | 28 September 2022 | 13 October 2022
S1045 | INCONTROLLER | malware--d3aa1058-b1b3-4c29-a3ba-9a9b90ccd93b | software | uses | T0836 | Modify Parameter | attack-pattern--097924ce-a9a9-4039-8591-e0deedfb8722 | technique | [INCONTROLLER](https://attack.mitre.org/software/S1045) can use the HTTP CGI scripts on Omron PLCs to modify parameters on EtherCat connected servo drives.(Citation: Wylie-22) | relationship--4dd93fd2-6e6d-4c50-a091-6d6ea6903f1e | 28 September 2022 | 13 October 2022
S1045 | INCONTROLLER | malware--d3aa1058-b1b3-4c29-a3ba-9a9b90ccd93b | software | uses | T0842 | Network Sniffing | attack-pattern--38213338-1aab-479d-949b-c81b66ccca5c | technique | [INCONTROLLER](https://attack.mitre.org/software/S1045) can deploy Tcpdump to sniff network traffic and collect PCAP files.(Citation: Wylie-22) | relationship--d8911566-f622-4a01-b765-514dbbfd8201 | 28 September 2022 | 13 October 2022
S1045 | INCONTROLLER | malware--d3aa1058-b1b3-4c29-a3ba-9a9b90ccd93b | software | uses | T0861 | Point & Tag Identification | attack-pattern--25852363-5968-4673-b81d-341d5ed90bd1 | technique | [INCONTROLLER](https://attack.mitre.org/software/S1045) can remotely read the OCP UA structure from devices.(Citation: CISA-AA22-103A) | relationship--064dfd6f-db5d-48e8-b350-9dd47a270911 | 28 September 2022 | 12 October 2022
S1045 | INCONTROLLER | malware--d3aa1058-b1b3-4c29-a3ba-9a9b90ccd93b | software | uses | T0843 | Program Download | attack-pattern--be69c571-d746-4b1f-bdd0-c0c9817e9068 | technique | [INCONTROLLER](https://attack.mitre.org/software/S1045) can use the CODESYS protocol to download programs to Schneider PLCs.(Citation: Wylie-22)(Citation: Brubaker-Incontroller) [INCONTROLLER](https://attack.mitre.org/software/S1045) can modified program logic on Omron PLCs using either the program download or backup transfer functions available through the HTTP server.(Citation: Wylie-22) | relationship--7c1eee62-3307-4e25-8a20-919ccd56ec1c | 29 September 2022 | 13 October 2022
S1045 | INCONTROLLER | malware--d3aa1058-b1b3-4c29-a3ba-9a9b90ccd93b | software | uses | T0845 | Program Upload | attack-pattern--3067b85e-271e-4bc5-81ad-ab1a81d411e3 | technique | [INCONTROLLER](https://attack.mitre.org/software/S1045) can use the CODESYS protocol to upload programs from Schneider PLCs.(Citation: Wylie-22)(Citation: Brubaker-Incontroller) [INCONTROLLER](https://attack.mitre.org/software/S1045) can obtain existing program logic from Omron PLCs by using either the program upload or backup functions available through the HTTP server.(Citation: Wylie-22) | relationship--b346eec8-de90-407c-b665-387086bb4553 | 29 September 2022 | 13 October 2022
S1045 | INCONTROLLER | malware--d3aa1058-b1b3-4c29-a3ba-9a9b90ccd93b | software | uses | T0886 | Remote Services | attack-pattern--e1f9cdd2-9511-4fca-90d7-f3e92cfdd0bf | technique | [INCONTROLLER](https://attack.mitre.org/software/S1045) can use the CODESYS protocol to remotely connect to Schneider PLCs and perform maintenance functions on the device.(Citation: Wylie-22) [INCONTROLLER](https://attack.mitre.org/software/S1045) can use Telnet to upload payloads and execute commands on Omron PLCs. (Citation: Brubaker-Incontroller)(Citation: Dragos-Pipedream) The malware can also use HTTP-based CGI scripts (e.g., cpu.fcgi, ecat.fcgi) to gain administrative access to the device.(Citation: Wylie-22) | relationship--2867f491-919b-463f-b689-bb3ceb7ae99f | 28 September 2022 | 13 October 2022
S1045 | INCONTROLLER | malware--d3aa1058-b1b3-4c29-a3ba-9a9b90ccd93b | software | uses | T0846 | Remote System Discovery | attack-pattern--d5a69cfb-fc2a-46cb-99eb-74b236db5061 | technique | [INCONTROLLER](https://attack.mitre.org/software/S1045) can perform a UDP multicast scan of UDP port 27127 to identify Schneider PLCs that use that port for the NetManage protocol.(Citation: Dragos-Pipedream)(Citation: Wylie-22) [INCONTROLLER](https://attack.mitre.org/software/S1045) can use the FINS (Factory Interface Network Service) protocol to scan for and obtain MAC address associated with Omron devices.(Citation: CISA-AA22-103A)(Citation: Wylie-22) [INCONTROLLER](https://attack.mitre.org/software/S1045) has the ability to perform scans for TCP port 4840 to identify devices running OPC UA servers.(Citation: Wylie-22) | relationship--66af47d7-c430-4ac9-8020-fd79b7059037 | 28 September 2022 | 13 October 2022
S1045 | INCONTROLLER | malware--d3aa1058-b1b3-4c29-a3ba-9a9b90ccd93b | software | uses | T0888 | Remote System Information Discovery | attack-pattern--2fedbe69-581f-447d-8a78-32ee7db939a9 | technique | [INCONTROLLER](https://attack.mitre.org/software/S1045) includes a library that creates Modbus connections with a device to request its device ID.(Citation: CISA-AA22-103A)(Citation: Wylie-22) | relationship--80a69b56-337d-446a-8167-8b9f63083c4f | 28 September 2022 | 13 October 2022
S1045 | INCONTROLLER | malware--d3aa1058-b1b3-4c29-a3ba-9a9b90ccd93b | software | uses | T0869 | Standard Application Layer Protocol | attack-pattern--e076cca8-2f08-45c9-aff7-ea5ac798b387 | technique | [INCONTROLLER](https://attack.mitre.org/software/S1045) can remotely send commands to a malicious agent uploaded on Omron PLCs over HTTP or HTTPS.(Citation: CISA-AA22-103A) | relationship--0d4f2f88-e176-42c7-8258-52b345045662 | 28 September 2022 | 12 October 2022
S1045 | INCONTROLLER | malware--d3aa1058-b1b3-4c29-a3ba-9a9b90ccd93b | software | uses | T0855 | Unauthorized Command Message | attack-pattern--40b300ba-f553-48bf-862e-9471b220d455 | technique | [INCONTROLLER](https://attack.mitre.org/software/S1045) can send custom Modbus commands to write register values on Schneider PLCs.(Citation: CISA-AA22-103A) [INCONTROLLER](https://attack.mitre.org/software/S1045) can send write tag values on OPC UA servers.(Citation: CISA-AA22-103A) | relationship--19c0d2bc-8de9-47c3-a1ee-63abc07c4348 | 28 September 2022 | 12 October 2022
S1045 | INCONTROLLER | malware--d3aa1058-b1b3-4c29-a3ba-9a9b90ccd93b | software | uses | T0859 | Valid Accounts | attack-pattern--cd2c76a4-5e23-4ca5-9c40-d5e0604f7101 | technique | [INCONTROLLER](https://attack.mitre.org/software/S1045) can brute force password-based authentication to Schneider PLCs over the CODESYS protocol (UDP port 1740).(Citation: CISA-AA22-103A) [INCONTROLLER](https://attack.mitre.org/software/S1045) can perform brute force guessing of passwords to OPC UA servers using a predefined list of passwords.(Citation: CISA-AA22-103A)(Citation: Wylie-22) | relationship--6681bc38-0b55-4714-b690-c609956b40bf | 28 September 2022 | 13 October 2022
S0604 | Industroyer | malware--e401d4fe-f0c9-44f0-98e6-f93487678808 | software | uses | T0800 | Activate Firmware Update Mode | attack-pattern--19a71d1e-6334-4233-8260-b749cae37953 | technique | The [Industroyer](https://attack.mitre.org/software/S0604) SIPROTEC DoS module places the victim device into firmware update mode. This is a legitimate use case under normal circumstances, but in this case is used the adversary to prevent the SIPROTEC from performing its designed protective functions. As a result the normal safeguards are disabled, leaving an unprotected link in the electric transmission. (Citation: Joe Slowik August 2019) | relationship--83c8c216-7ff7-4bd3-9db4-573469628d95 | 17 October 2018 | 25 September 2023
S0604 | Industroyer | malware--e401d4fe-f0c9-44f0-98e6-f93487678808 | software | uses | T0802 | Automated Collection | attack-pattern--3de230d4-3e42-4041-b089-17e1128feded | technique | [Industroyer](https://attack.mitre.org/software/S0604) automatically collects protocol object data to learn about control devices in the environment. (Citation: Anton Cherepanov, ESET June 2017) | relationship--c4122b58-f1b2-4656-a715-55016700bf75 | 17 October 2018 | 23 September 2022
S0604 | Industroyer | malware--e401d4fe-f0c9-44f0-98e6-f93487678808 | software | uses | T0803 | Block Command Message | attack-pattern--008b8f56-6107-48be-aa9f-746f927dbb61 | technique | In [Industroyer](https://attack.mitre.org/software/S0604) the first COM port from the configuration file is used for the actual communication and the two other COM ports are just opened to prevent other processes accessing them. Thus, the IEC 101 payload component is able to take over and maintain control of the RTU device. (Citation: Anton Cherepanov, ESET June 2017) | relationship--c785c026-4139-4c56-a6dd-cdd3ba75bab1 | 17 October 2018 | 23 September 2022
S0604 | Industroyer | malware--e401d4fe-f0c9-44f0-98e6-f93487678808 | software | uses | T0804 | Block Reporting Message | attack-pattern--3f1f4ccb-9be2-4ff8-8f69-dd972221169b | technique | [Industroyer](https://attack.mitre.org/software/S0604) uses the first COM port from the configuration file for the communication and the other two COM ports are opened to prevent other processes accessing them. This may block processes or operators from getting reporting messages from a device. (Citation: Anton Cherepanov, ESET June 2017) | relationship--648c6649-5861-4b43-a7e5-a9665bafb576 | 17 October 2018 | 23 September 2022
S0604 | Industroyer | malware--e401d4fe-f0c9-44f0-98e6-f93487678808 | software | uses | T0805 | Block Serial COM | attack-pattern--1c478716-71d9-46a4-9a53-fa5d576adb60 | technique | In [Industroyer](https://attack.mitre.org/software/S0604) the first COM port from the configuration file is used for the actual communication and the two other COM ports are just opened to prevent other processes accessing them. Thus, the IEC 101 payload component is able to take over and maintain control of the RTU device. (Citation: Anton Cherepanov, ESET June 2017) | relationship--8a604466-8437-4fe6-b6db-ec8fb05d702a | 17 October 2018 | 23 September 2022
S0604 | Industroyer | malware--e401d4fe-f0c9-44f0-98e6-f93487678808 | software | uses | T0806 | Brute Force I/O | attack-pattern--8e7089d3-fba2-44f8-94a8-9a79c53920c4 | technique | The [Industroyer](https://attack.mitre.org/software/S0604) IEC 104 module has 3 modes available to perform its attack. These modes are range, shift, and sequence. The range mode operates in 2 stages. The first stage of range mode gathers Information Object Addresses (IOA) and sends select and execute packets to switch the state. The second stage of range mode has an infinite loop where it will switch the state of all of the previously discovered IOAs. Shift mode is similar to range mode, but instead of staying within the same range, it will add a shift value to the default range values. (Citation: Anton Cherepanov, ESET June 2017) | relationship--966b59c0-8641-432c-84f7-b2a712004d74 | 17 October 2018 | 23 September 2022
S0604 | Industroyer | malware--e401d4fe-f0c9-44f0-98e6-f93487678808 | software | uses | T0807 | Command-Line Interface | attack-pattern--24a9253e-8948-4c98-b751-8e2aee53127c | technique | The name of the [Industroyer](https://attack.mitre.org/software/S0604) payload DLL is supplied by the attackers via a command line parameter supplied in one of the main backdoors execute a shell command commands. (Citation: Anton Cherepanov, ESET June 2017) | relationship--3be8045a-1f0d-4460-a76b-ae830e74c1e0 | 17 October 2018 | 12 October 2022
S0604 | Industroyer | malware--e401d4fe-f0c9-44f0-98e6-f93487678808 | software | uses | T0884 | Connection Proxy | attack-pattern--d67adac8-e3b9-44f9-9e6d-6c2a7d69dbe4 | technique | [Industroyer](https://attack.mitre.org/software/S0604) attempts to connect with a hardcoded internal proxy on TCP 3128 [default Squid proxy]. If established, the backdoor attempts to reach an external C2 server via the internal proxy. (Citation: Dragos Inc. June 2017) | relationship--433539bf-cb17-4de1-9c0f-e579b041514f | 17 October 2018 | 23 September 2022
S0604 | Industroyer | malware--e401d4fe-f0c9-44f0-98e6-f93487678808 | software | uses | T0809 | Data Destruction | attack-pattern--493832d9-cea6-4b63-abe7-9a65a6473675 | technique | [Industroyer](https://attack.mitre.org/software/S0604) has a destructive wiper that overwrites all ICS configuration files across the hard drives and all mapped network drives specifically targeting ABB PCM600 configuration files. (Citation: Dragos Inc. June 2017) | relationship--a1cbbdb5-30ad-4139-9784-e5a134f8d405 | 17 October 2018 | 23 September 2022
S0604 | Industroyer | malware--e401d4fe-f0c9-44f0-98e6-f93487678808 | software | uses | T0813 | Denial of Control | attack-pattern--e33c7ecc-5a38-497f-beb2-a9a2049a4c20 | technique | [Industroyer](https://attack.mitre.org/software/S0604) is able to block serial COM channels temporarily causing a denial of control. (Citation: Anton Cherepanov, ESET June 2017) | relationship--9902691c-aaf2-48a1-b1ca-cd6f652ae1c6 | 17 October 2018 | 23 September 2022
S0604 | Industroyer | malware--e401d4fe-f0c9-44f0-98e6-f93487678808 | software | uses | T0814 | Denial of Service | attack-pattern--1b22b676-9347-4c55-9a35-ef0dc653db5b | technique | The [Industroyer](https://attack.mitre.org/software/S0604) SIPROTEC DoS module exploits the CVE-2015-5374 vulnerability in order to render a Siemens SIPROTEC device unresponsive. Once this vulnerability is successfully exploited, the target device stops responding to any commands until it is rebooted manually. (Citation: Anton Cherepanov, ESET June 2017) Once the tool is executed it sends specifically crafted packets to port 50,000 of the target IP addresses using UDP. The UDP packet contains the following 18 byte payload: 0x11 49 00 00 00 00 00 00 00 00 00 00 00 00 00 00 28 9E. (Citation: Anton Cherepanov, ESET June 2017) | relationship--50c20664-75dc-451e-b026-67b1d309e4b5 | 17 October 2018 | 23 September 2022
S0604 | Industroyer | malware--e401d4fe-f0c9-44f0-98e6-f93487678808 | software | uses | T0815 | Denial of View | attack-pattern--56ddc820-6cfb-407f-850b-52c035d123ac | technique | [Industroyer](https://attack.mitre.org/software/S0604) is able to block serial COM channels temporarily causing a denial of view. (Citation: Anton Cherepanov, ESET June 2017) | relationship--a04169ed-c16b-466b-80ef-22a11067f475 | 17 October 2018 | 23 September 2022
S0604 | Industroyer | malware--e401d4fe-f0c9-44f0-98e6-f93487678808 | software | uses | T0816 | Device Restart/Shutdown | attack-pattern--25dfc8ad-bd73-4dfd-84a9-3c3d383f76e9 | technique | The [Industroyer](https://attack.mitre.org/software/S0604) SIPROTEC DoS module exploits the CVE-2015-5374 vulnerability in order to render a Siemens SIPROTEC device unresponsive. While the vulnerability does not directly cause the restart or shutdown of the device, the device must be restarted manually before it can resume operations. (Citation: Anton Cherepanov, ESET June 2017) | relationship--87c8ab74-576d-4962-b641-0762d374d1e8 | 17 October 2018 | 23 September 2022
S0604 | Industroyer | malware--e401d4fe-f0c9-44f0-98e6-f93487678808 | software | uses | T0827 | Loss of Control | attack-pattern--a81696ef-c106-482c-8f80-59c30f2569fb | technique | [Industroyer](https://attack.mitre.org/software/S0604)'s data wiper component removes the registry image path throughout the system and overwrites all files, rendering the system unusable. (Citation: Anton Cherepanov, ESET June 2017) | relationship--a6d8b66d-fc10-404f-b0ae-e8c66506b818 | 17 October 2018 | 31 March 2023
S0604 | Industroyer | malware--e401d4fe-f0c9-44f0-98e6-f93487678808 | software | uses | T0837 | Loss of Protection | attack-pattern--2bb4d762-bf4a-4bc3-9318-15cc6a354163 | technique | [Industroyer](https://attack.mitre.org/software/S0604) contained a module which leveraged a vulnerability in the Siemens SIPROTEC relays (CVE-2015-5374) to create a Denial of Service against automated protective relays. (Citation: Joe Slowik August 2019) | relationship--f347b4fe-d829-427d-851a-fff3393441db | 12 April 2021 | 14 April 2023
S0604 | Industroyer | malware--e401d4fe-f0c9-44f0-98e6-f93487678808 | software | uses | T0829 | Loss of View | attack-pattern--138979ba-0430-4de6-a128-2fc0b056ba36 | technique | [Industroyer](https://attack.mitre.org/software/S0604)'s data wiper component removes the registry image path throughout the system and overwrites all files, rendering the system unusable. (Citation: Anton Cherepanov, ESET June 2017) | relationship--9d6f9bba-dd79-4cb6-a0f3-1284e58a6236 | 17 October 2018 | 23 September 2022
S0604 | Industroyer | malware--e401d4fe-f0c9-44f0-98e6-f93487678808 | software | uses | T0831 | Manipulation of Control | attack-pattern--1af9e3fd-2bcc-414d-adbd-fe3b95c02ca1 | technique | [Industroyer](https://attack.mitre.org/software/S0604) toggles breakers to the open state utilizing unauthorized command messages. (Citation: Anton Cherepanov, ESET June 2017) | relationship--7c3b65e8-e8b7-4c3b-b27b-e216986d8976 | 17 October 2018 | 23 September 2022
S0604 | Industroyer | malware--e401d4fe-f0c9-44f0-98e6-f93487678808 | software | uses | T0832 | Manipulation of View | attack-pattern--4c2e1408-9d68-4187-8e6b-a77bc52700ec | technique | [Industroyer](https://attack.mitre.org/software/S0604)'s OPC module can brute force values and will send out a 0x01 status which for the target systems equates to a Primary Variable Out of Limits misdirecting operators from understanding protective relay status. (Citation: Anton Cherepanov, ESET June 2017) | relationship--ca3c4d4b-cf53-4489-904f-8a220e421aeb | 17 October 2018 | 31 March 2023
S0604 | Industroyer | malware--e401d4fe-f0c9-44f0-98e6-f93487678808 | software | uses | T0801 | Monitor Process State | attack-pattern--2d0d40ad-22fa-4cc8-b264-072557e1364b | technique | [Industroyer](https://attack.mitre.org/software/S0604)'s OPC and IEC 61850 protocol modules include the ability to send stVal requests to read the status of operational variables. (Citation: Anton Cherepanov, ESET June 2017) | relationship--83c29179-4805-403a-acf5-5151c4d2e556 | 17 October 2018 | 23 September 2022
S0604 | Industroyer | malware--e401d4fe-f0c9-44f0-98e6-f93487678808 | software | uses | T0840 | Network Connection Enumeration | attack-pattern--ea0c980c-5cf0-43a7-a049-59c4c207566e | technique | [Industroyer](https://attack.mitre.org/software/S0604) contains an IEC 61850 module that enumerates all connected network adapters to determine their TCP/IP subnet masks. (Citation: Anton Cherepanov, ESET June 2017) | relationship--841ec349-0f4c-43fa-89b8-ef3656497fc9 | 17 October 2018 | 23 September 2022
S0604 | Industroyer | malware--e401d4fe-f0c9-44f0-98e6-f93487678808 | software | uses | T0846 | Remote System Discovery | attack-pattern--d5a69cfb-fc2a-46cb-99eb-74b236db5061 | technique | The [Industroyer](https://attack.mitre.org/software/S0604) IEC 61850 payload component has the ability to discover relevant devices in the infected host's network subnet by attempting to connect on port 102.(Citation: Anton Cherepanov, ESET June 2017) [Industroyer](https://attack.mitre.org/software/S0604) contains an OPC DA module that enumerates all OPC servers using the `ICatInformation::EnumClassesOfCategories` method with `CATID_OPCDAServer20` category identifier and `IOPCServer::GetStatus` to identify the ones running. | relationship--1c831708-28c2-47ae-a158-39f1f7b73406 | 17 October 2018 | 29 September 2022
S0604 | Industroyer | malware--e401d4fe-f0c9-44f0-98e6-f93487678808 | software | uses | T0888 | Remote System Information Discovery | attack-pattern--2fedbe69-581f-447d-8a78-32ee7db939a9 | technique | The [Industroyer](https://attack.mitre.org/software/S0604) IEC 61850 component sends the domain-specific MMSgetNameList request to determine what logical nodes the device supports. It then searches the logical nodes for the CSW value, which indicates the device performs a circuit breaker or switch control function.(Citation: ESET Industroyer) [Industroyer](https://attack.mitre.org/software/S0604)'s OPC DA module also uses IOPCBrowseServerAddressSpace to look for items with the following strings: ctlSelOn, ctlOperOn, ctlSelOff, ctlOperOff, Pos and stVal.(Citation: ESET Industroyer) [Industroyer](https://attack.mitre.org/software/S0604) IEC 60870-5-104 module includes a range mode to discover Information Object Addresses (IOAs) by enumerating through each.(Citation: ESET Industroyer) | relationship--62e818b8-38e6-42ff-9424-9a327332eb2a | 29 September 2022 | 17 March 2023
S0604 | Industroyer | malware--e401d4fe-f0c9-44f0-98e6-f93487678808 | software | uses | T0881 | Service Stop | attack-pattern--063b5b92-5361-481a-9c3f-95492ed9a2d8 | technique | [Industroyer](https://attack.mitre.org/software/S0604) has the capability to stop a service itself, or to login as a user and stop a service as that user. (Citation: Anton Cherepanov, ESET June 2017) | relationship--66f79019-d52c-46a6-b605-c2335d1d3d20 | 17 October 2018 | 23 September 2022
S0604 | Industroyer | malware--e401d4fe-f0c9-44f0-98e6-f93487678808 | software | uses | T0855 | Unauthorized Command Message | attack-pattern--40b300ba-f553-48bf-862e-9471b220d455 | technique | Using its protocol payloads, [Industroyer](https://attack.mitre.org/software/S0604) sends unauthorized commands to RTUs to change the state of equipment. (Citation: Anton Cherepanov, ESET June 2017) | relationship--9fb2a9b2-3b25-4f77-9f7a-e832b2e5071a | 17 October 2018 | 23 September 2022
S1072 | Industroyer2 | malware--6a0d0ea9-b2c4-43fe-a552-ac41a3009dc5 | software | uses | T0802 | Automated Collection | attack-pattern--3de230d4-3e42-4041-b089-17e1128feded | technique | [Industroyer2](https://attack.mitre.org/software/S1072) leverages a hardcoded list of remote-station IP addresses to iteratively initiate communications and collect information across multiple priority IEC-104 priority levels.(Citation: Industroyer2 Forescout July 2022) | relationship--6ff846b1-9444-45f1-837a-4eeeb16bdfe7 | 30 March 2023 | 30 March 2023
S1072 | Industroyer2 | malware--6a0d0ea9-b2c4-43fe-a552-ac41a3009dc5 | software | uses | T0806 | Brute Force I/O | attack-pattern--8e7089d3-fba2-44f8-94a8-9a79c53920c4 | technique | [Industroyer2](https://attack.mitre.org/software/S1072) can iterate across a device’s IOAs to modify the ON/OFF value of a given IO state.(Citation: Industroyer2 Mandiant April 2022)(Citation: Industroyer2 Forescout July 2022) | relationship--2087b2b9-3b30-45be-abcd-4320bf0fa66b | 30 March 2023 | 06 April 2023
S1072 | Industroyer2 | malware--6a0d0ea9-b2c4-43fe-a552-ac41a3009dc5 | software | uses | T0836 | Modify Parameter | attack-pattern--097924ce-a9a9-4039-8591-e0deedfb8722 | technique | [Industroyer2](https://attack.mitre.org/software/S1072) modifies specified Information Object Addresses (IOAs) for specified Application Service Data Unit (ASDU) addresses to either the ON or OFF state.(Citation: Industroyer2 Mandiant April 2022)(Citation: Industroyer2 Forescout July 2022) | relationship--665587ee-1524-4334-9580-2b448c417542 | 30 March 2023 | 06 April 2023
S1072 | Industroyer2 | malware--6a0d0ea9-b2c4-43fe-a552-ac41a3009dc5 | software | uses | T0801 | Monitor Process State | attack-pattern--2d0d40ad-22fa-4cc8-b264-072557e1364b | technique | [Industroyer2](https://attack.mitre.org/software/S1072) uses a General Interrogation command to monitor the device’s Information Object Addresses (IOAs) and their IO state values.(Citation: Industroyer2 Forescout July 2022) | relationship--730580d4-d68c-407f-9d09-f379e9aefc7e | 30 March 2023 | 30 March 2023
S1072 | Industroyer2 | malware--6a0d0ea9-b2c4-43fe-a552-ac41a3009dc5 | software | uses | T0888 | Remote System Information Discovery | attack-pattern--2fedbe69-581f-447d-8a78-32ee7db939a9 | technique | [Industroyer2](https://attack.mitre.org/software/S1072) has the capability to poll a target device about its connection status, data transfer status, Common Address (CA), Information Object Addresses (IOAs), and IO state values across multiple priority levels.(Citation: Industroyer2 Forescout July 2022)(Citation: Industroyer2 ESET April 2022) | relationship--67e11f38-9f68-4989-8de3-da65af52063e | 30 March 2023 | 06 April 2023
S1072 | Industroyer2 | malware--6a0d0ea9-b2c4-43fe-a552-ac41a3009dc5 | software | uses | T0881 | Service Stop | attack-pattern--063b5b92-5361-481a-9c3f-95492ed9a2d8 | technique | [Industroyer2](https://attack.mitre.org/software/S1072) has the capability to terminate specified processes (i.e., PServiceControl.exe and PService_PDD.exe) and rename each process to prevent restart. These are defined through a hardcoded configuration.(Citation: Industroyer2 Mandiant April 2022) | relationship--54a977df-ca85-43b2-b2bc-96fdcd23aa9b | 30 March 2023 | 31 March 2023
S1072 | Industroyer2 | malware--6a0d0ea9-b2c4-43fe-a552-ac41a3009dc5 | software | uses | T0855 | Unauthorized Command Message | attack-pattern--40b300ba-f553-48bf-862e-9471b220d455 | technique | [Industroyer2](https://attack.mitre.org/software/S1072) is capable of sending command messages from the compromised device to target remote stations to open data channels, retrieve the location and values of Information Object Addresses (IOAs), and modify the IO state values through Select Before Operate I/O, Select/Execute, and Invert Default State operations.(Citation: Industroyer2 Mandiant April 2022)(Citation: Industroyer2 Forescout July 2022) | relationship--6a5922e1-e282-464d-9e71-ce2c2ed44908 | 30 March 2023 | 06 April 2023
S0607 | KillDisk | malware--e221eb77-1502-4129-af1d-fe1ad55e7ec6 | software | uses | T0809 | Data Destruction | attack-pattern--493832d9-cea6-4b63-abe7-9a65a6473675 | technique | [KillDisk](https://attack.mitre.org/software/S0607) is able to delete system files to make the system unbootable and targets 35 different types of files for deletion. (Citation: Anton Cherepanov) | relationship--b252a076-6d4e-49f5-95ac-16264ef05b1d | 14 December 2017 | 12 October 2022
S0607 | KillDisk | malware--e221eb77-1502-4129-af1d-fe1ad55e7ec6 | software | uses | T0872 | Indicator Removal on Host | attack-pattern--53a26eee-1080-4d17-9762-2027d5a1b805 | technique | [KillDisk](https://attack.mitre.org/software/S0607) deletes application, security, setup, and system event logs from Windows systems. (Citation: Anton Cherepanov) | relationship--ab8e129c-5411-4784-9194-068fa915da23 | 14 December 2017 | 12 October 2022
S0607 | KillDisk | malware--e221eb77-1502-4129-af1d-fe1ad55e7ec6 | software | uses | T0829 | Loss of View | attack-pattern--138979ba-0430-4de6-a128-2fc0b056ba36 | technique | [KillDisk](https://attack.mitre.org/software/S0607) erases the master boot record (MBR) and system logs, leaving the system unusable. (Citation: Booz Allen Hamilton) | relationship--04bf72de-75ba-4d95-ad24-f93ad835180c | 14 December 2017 | 12 October 2022
S0607 | KillDisk | malware--e221eb77-1502-4129-af1d-fe1ad55e7ec6 | software | uses | T0881 | Service Stop | attack-pattern--063b5b92-5361-481a-9c3f-95492ed9a2d8 | technique | [KillDisk](https://attack.mitre.org/software/S0607) looks for and terminates two non-standard processes, one of which is an ICS application. (Citation: Anton Cherepanov) | relationship--b452a076-6d4e-49f5-95ac-16264ef05b1d | 14 December 2017 | 12 October 2022
S0372 | LockerGoga | malware--5af7a825-2d9f-400d-931a-e00eb9e27f48 | software | uses | T0827 | Loss of Control | attack-pattern--a81696ef-c106-482c-8f80-59c30f2569fb | technique | Some of Norsk Hydro's production systems were impacted by a [LockerGoga](https://attack.mitre.org/software/S0372) infection. This resulted in a loss of control which forced the company to switch to manual operations. (Citation: Kevin Beaumont) (Citation: Hydro) | relationship--b5ab26e2-eb90-4f19-b35a-b8a0a5438961 | 14 December 2017 | 12 October 2022
S0372 | LockerGoga | malware--5af7a825-2d9f-400d-931a-e00eb9e27f48 | software | uses | T0828 | Loss of Productivity and Revenue | attack-pattern--63b6942d-8359-4506-bfb3-cf87aa8120ee | technique | While Norsk Hydro attempted to recover from a [LockerGoga](https://attack.mitre.org/software/S0372) infection, most of its 160 manufacturing locations switched to manual (non-IT driven) operations. Manual operations can result in a loss of productivity. (Citation: Kevin Beaumont)(Citation: Hydro) | relationship--46bc86e4-e20b-4778-80d2-8891039e6fb4 | 14 December 2017 | 12 October 2022
S0372 | LockerGoga | malware--5af7a825-2d9f-400d-931a-e00eb9e27f48 | software | uses | T0829 | Loss of View | attack-pattern--138979ba-0430-4de6-a128-2fc0b056ba36 | technique | Some of Norsk Hydro's production systems were impacted by a [LockerGoga](https://attack.mitre.org/software/S0372) infection. This resulted in a loss of view which forced the company to switch to manual operations. (Citation: Kevin Beaumont) (Citation: Hydro) | relationship--7a55fc66-0d5c-4ef6-af28-d4a4bb84381d | 14 December 2017 | 12 October 2022
S0368 | NotPetya | malware--5719af9d-6b16-46f9-9b28-fb019541ddbb | software | uses | T0866 | Exploitation of Remote Services | attack-pattern--85a45294-08f1-4539-bf00-7da08aa7b0ee | technique | [NotPetya](https://attack.mitre.org/software/S0368) initially infected IT networks, but by means of an exploit (particularly the SMBv1-targeting MS17-010 vulnerability) spread to industrial networks. (Citation: Joe Slowik April 2019) | relationship--6603a100-d655-4e6b-8d38-73c11b89dde4 | 26 March 2019 | 12 October 2022
S0368 | NotPetya | malware--5719af9d-6b16-46f9-9b28-fb019541ddbb | software | uses | T0867 | Lateral Tool Transfer | attack-pattern--ead7bd34-186e-4c79-9a4d-b65bcce6ed9d | technique | [NotPetya](https://attack.mitre.org/software/S0368) can move laterally through industrial networks by means of the SMB service. (Citation: Joe Slowik April 2019) | relationship--6258c355-677c-452d-b1fc-27767232437b | 26 March 2019 | 12 October 2022
S0368 | NotPetya | malware--5719af9d-6b16-46f9-9b28-fb019541ddbb | software | uses | T0828 | Loss of Productivity and Revenue | attack-pattern--63b6942d-8359-4506-bfb3-cf87aa8120ee | technique | [NotPetya](https://attack.mitre.org/software/S0368) disrupted manufacturing facilities supplying vaccines, resulting in a halt of production and the inability to meet demand for specific vaccines. (Citation: David Voreacos, Katherine Chinglinsky, Riley Griffin December 2019) | relationship--7258c355-677c-452d-b1fc-27767232437b | 26 March 2019 | 12 October 2022
S1006 | PLC-Blaster | malware--4dcff507-5af8-47ce-964a-8d9569e9ccfe | software | uses | T0858 | Change Operating Mode | attack-pattern--2883c520-7957-46ca-89bd-dab1ad53b601 | technique | [PLC-Blaster](https://attack.mitre.org/software/S1006) stops the execution of the user program on the target to enable the transfer of its own code. The worm then copies itself to the target and subsequently starts the target PLC again. (Citation: Spenneberg, Ralf, Maik Brggemann, and Hendrik Schwartke March 2016) | relationship--a4c81fe6-1ad9-4bba-a415-a3c099eaa2be | 13 April 2021 | 12 October 2022
S1006 | PLC-Blaster | malware--4dcff507-5af8-47ce-964a-8d9569e9ccfe | software | uses | T0814 | Denial of Service | attack-pattern--1b22b676-9347-4c55-9a35-ef0dc653db5b | technique | The execution on the PLC can be stopped by violating the cycle time limit. The [PLC-Blaster](https://attack.mitre.org/software/S1006) implements an endless loop triggering an error condition within the PLC with the impact of a DoS. (Citation: Spenneberg, Ralf, Maik Brggemann, and Hendrik Schwartke March 2016) | relationship--535c5160-17e0-44eb-9f4b-1a8e216b56a2 | 17 October 2018 | 12 October 2022
S1006 | PLC-Blaster | malware--4dcff507-5af8-47ce-964a-8d9569e9ccfe | software | uses | T0835 | Manipulate I/O Image | attack-pattern--36e9f5bc-ac13-4da4-a2f4-01f4877d9004 | technique | [PLC-Blaster](https://attack.mitre.org/software/S1006) may manipulate any outputs of the PLC. Using the POU POKE any value within the process image may be modified. (Citation: Spenneberg, Ralf, Maik Brggemann, and Hendrik Schwartke March 2016) | relationship--6fa3aee4-2a29-4c0f-9e61-1f7df5eccc00 | 17 October 2018 | 12 October 2022
S1006 | PLC-Blaster | malware--4dcff507-5af8-47ce-964a-8d9569e9ccfe | software | uses | T0821 | Modify Controller Tasking | attack-pattern--09a61657-46e1-439e-b3ed-3e4556a78243 | technique | [PLC-Blaster](https://attack.mitre.org/software/S1006)'s code is stored in OB9999. The original code on the target is untouched. The OB is automatically detected by the PLC and executed. (Citation: Spenneberg, Ralf, Maik Brggemann, and Hendrik Schwartke March 2016) | relationship--20f66fab-7a08-4707-ac79-92dac5acd11d | 13 April 2021 | 12 October 2022
S1006 | PLC-Blaster | malware--4dcff507-5af8-47ce-964a-8d9569e9ccfe | software | uses | T0889 | Modify Program | attack-pattern--fc5fda7e-6b2c-4457-b036-759896a2efa2 | technique | [PLC-Blaster](https://attack.mitre.org/software/S1006) copies itself to various Program Organization Units (POU) on the target device. The POUs include the Data Block, Function, and Function Block. (Citation: Spenneberg, Ralf, Maik Brggemann, and Hendrik Schwartke March 2016) | relationship--9515f24c-1c33-4197-b9c9-b9992bc696ca | 13 April 2021 | 12 October 2022
S1006 | PLC-Blaster | malware--4dcff507-5af8-47ce-964a-8d9569e9ccfe | software | uses | T0834 | Native API | attack-pattern--b52870cc-83f3-473c-b895-72d91751030b | technique | [PLC-Blaster](https://attack.mitre.org/software/S1006) uses the system function blocks TCON and TDISCON to initiate and destroy TCP connections to arbitrary systems. Buffers may be sent and received on these connections with TRCV und TSEND system function blocks. (Citation: Spenneberg, Ralf, Maik Brggemann, and Hendrik Schwartke March 2016) | relationship--21041206-da58-45c7-adb0-db07caebdcb6 | 13 April 2021 | 12 October 2022
S1006 | PLC-Blaster | malware--4dcff507-5af8-47ce-964a-8d9569e9ccfe | software | uses | T0843 | Program Download | attack-pattern--be69c571-d746-4b1f-bdd0-c0c9817e9068 | technique | [PLC-Blaster](https://attack.mitre.org/software/S1006) utilizes the PLC communication and management API to load executable Program Organization Units. (Citation: Spenneberg, Ralf, Maik Brggemann, and Hendrik Schwartke March 2016) | relationship--31897c41-1d47-4a34-b531-21c3f74651a8 | 13 April 2021 | 12 October 2022
S1006 | PLC-Blaster | malware--4dcff507-5af8-47ce-964a-8d9569e9ccfe | software | uses | T0846 | Remote System Discovery | attack-pattern--d5a69cfb-fc2a-46cb-99eb-74b236db5061 | technique | [PLC-Blaster](https://attack.mitre.org/software/S1006) scans the network to find other Siemens S7 PLC devices to infect. It locates these devices by checking for a service listening on TCP port 102. (Citation: Spenneberg, Ralf, Maik Brggemann, and Hendrik Schwartke March 2016) | relationship--5c0bdf4c-233f-42cd-8900-2a5cc8c9387c | 17 October 2018 | 12 October 2022
S0496 | REvil | malware--ac61f1f9-7bb1-465e-9b8a-c2ce8e88baf5 | software | uses | T0828 | Loss of Productivity and Revenue | attack-pattern--63b6942d-8359-4506-bfb3-cf87aa8120ee | technique | The [REvil](https://attack.mitre.org/software/S0496) malware gained access to an organizations network and encrypted sensitive files used by OT equipment. (Citation: Selena Larson, Camille Singleton December 2020) | relationship--ab306654-2abb-4983-8d30-df4058adb06c | 12 April 2021 | 12 October 2022
S0496 | REvil | malware--ac61f1f9-7bb1-465e-9b8a-c2ce8e88baf5 | software | uses | T0849 | Masquerading | attack-pattern--ba203963-3182-41ac-af14-7e7ebc83cd61 | technique | [REvil](https://attack.mitre.org/software/S0496) searches for whether the Ahnlab autoup.exe service is running on the target system and injects its payload into this existing process. (Citation: Tom Fakterman August 2019) | relationship--5e099568-fb5c-4f58-af7e-4e1b7a9d1128 | 12 April 2021 | 12 October 2022
S0496 | REvil | malware--ac61f1f9-7bb1-465e-9b8a-c2ce8e88baf5 | software | uses | T0886 | Remote Services | attack-pattern--e1f9cdd2-9511-4fca-90d7-f3e92cfdd0bf | technique | [REvil](https://attack.mitre.org/software/S0496) uses the SMB protocol to encrypt files located on remotely connected file shares. (Citation: Max Heinemeyer February 2020) | relationship--e323dee4-a896-4a82-85f5-d51d311b0437 | 12 April 2021 | 12 October 2022
S0496 | REvil | malware--ac61f1f9-7bb1-465e-9b8a-c2ce8e88baf5 | software | uses | T0853 | Scripting | attack-pattern--2dc2b567-8821-49f9-9045-8740f3d0b958 | technique | [REvil](https://attack.mitre.org/software/S0496) utilizes JavaScript, WScript, and PowerShell scripts to execute. The malicious JavaScript attachment has an obfuscated PowerShell script that executes the malware. (Citation: Tom Fakterman August 2019) | relationship--ee1bf429-2c7c-4eb6-acca-e758522baf2e | 12 April 2021 | 12 October 2022
S0496 | REvil | malware--ac61f1f9-7bb1-465e-9b8a-c2ce8e88baf5 | software | uses | T0881 | Service Stop | attack-pattern--063b5b92-5361-481a-9c3f-95492ed9a2d8 | technique | [REvil](https://attack.mitre.org/software/S0496) searches for all processes listed in the prc field within its configuration file and then terminates each process. (Citation: McAfee Labs October 2019) | relationship--309e4558-e591-4d03-9bb9-07d30acf011f | 12 April 2021 | 12 October 2022
S0496 | REvil | malware--ac61f1f9-7bb1-465e-9b8a-c2ce8e88baf5 | software | uses | T0869 | Standard Application Layer Protocol | attack-pattern--e076cca8-2f08-45c9-aff7-ea5ac798b387 | technique | [REvil](https://attack.mitre.org/software/S0496) sends HTTPS POST messages with randomly generated URLs to communicate with a remote server. (Citation: Tom Fakterman August 2019) (Citation: SecureWorks September 2019) | relationship--c90cfddb-253b-41c8-9057-2abde6f8aa6d | 12 April 2021 | 12 October 2022
S0496 | REvil | malware--ac61f1f9-7bb1-465e-9b8a-c2ce8e88baf5 | software | uses | T0882 | Theft of Operational Information | attack-pattern--b7e13ee8-182c-4f19-92a4-a88d7d855d54 | technique | [REvil](https://attack.mitre.org/software/S0496) sends exfiltrated data from the victims system using HTTPS POST messages sent to the C2 system. (Citation: McAfee Labs October 2019) (Citation: SecureWorks September 2019) | relationship--6ed07095-c23a-4676-807f-a544deaeb274 | 12 April 2021 | 12 October 2022
S0496 | REvil | malware--ac61f1f9-7bb1-465e-9b8a-c2ce8e88baf5 | software | uses | T0863 | User Execution | attack-pattern--2736b752-4ec5-4421-a230-8977dea7649c | technique | [REvil](https://attack.mitre.org/software/S0496) initially executes when the user clicks on a JavaScript file included in the phishing emails .zip attachment. (Citation: Tom Fakterman August 2019) | relationship--1fd4cf4e-a26c-4fe5-a7fd-f49b8aea8437 | 12 April 2021 | 12 October 2022
S0446 | Ryuk | malware--a020a61c-423f-4195-8c46-ba1d21abba37 | software | uses | T0828 | Loss of Productivity and Revenue | attack-pattern--63b6942d-8359-4506-bfb3-cf87aa8120ee | technique | An enterprise resource planning (ERP) manufacturing server was lost to the [Ryuk](https://attack.mitre.org/software/S0446) attack. The manufacturing process had to rely on paper and existing orders to keep the shop floor open. (Citation: Kelly Jackson Higgins) | relationship--383e242a-72d4-4b40-8905-888595c34919 | 14 December 2017 | 12 October 2022
S0603 | Stuxnet | malware--088f1d6e-0783-47c6-9923-9c79b2af43d4 | software | uses | T0807 | Command-Line Interface | attack-pattern--24a9253e-8948-4c98-b751-8e2aee53127c | technique | [Stuxnet](https://attack.mitre.org/software/S0603) will store and execute SQL code that will extract and execute Stuxnet from the saved CAB file using xp_cmdshell with the following command: `set @s = master..xp _ cmdshell extrac32 /y +@t+ +@t+x; exec(@s);` (Citation: Nicolas Falliere, Liam O Murchu, Eric Chien February 2011) | relationship--6baa9172-04e4-416d-a009-668cda23fd5d | 08 October 2021 | 19 October 2022
S0603 | Stuxnet | malware--088f1d6e-0783-47c6-9923-9c79b2af43d4 | software | uses | T0885 | Commonly Used Port | attack-pattern--e6c31185-8040-4267-83d3-b217b8a92f07 | technique | [Stuxnet](https://attack.mitre.org/software/S0603) attempts to contact command and control servers on port 80 to send basic information about the computer it has compromised. (Citation: Nicolas Falliere, Liam O Murchu, Eric Chien February 2011) | relationship--bcece7ce-91b5-40b3-b87a-25cab3600e5c | 14 December 2017 | 20 September 2022
S0603 | Stuxnet | malware--088f1d6e-0783-47c6-9923-9c79b2af43d4 | software | uses | T0866 | Exploitation of Remote Services | attack-pattern--85a45294-08f1-4539-bf00-7da08aa7b0ee | technique | [Stuxnet](https://attack.mitre.org/software/S0603) executes malicious SQL commands in the WinCC database server to propagate to remote systems. The malicious SQL commands include xp_cmdshell, sp_dumpdbilog, and sp_addextendedproc. (Citation: Nicolas Falliere, Liam O Murchu, Eric Chien February 2011) | relationship--be532c78-daf5-431b-adae-ab11af395513 | 14 December 2017 | 20 September 2022
S0603 | Stuxnet | malware--088f1d6e-0783-47c6-9923-9c79b2af43d4 | software | uses | T0891 | Hardcoded Credentials | attack-pattern--c9a8d958-fcdb-40d2-af4c-461c8031651a | technique | [Stuxnet](https://attack.mitre.org/software/S0603) uses a hardcoded password in the WinCC software's database server as one of the mechanisms used to propagate to nearby systems. (Citation: Nicolas Falliere, Liam O Murchu, Eric Chien February 2011) | relationship--874752f4-59a2-46e9-ae28-befe0142b223 | 14 December 2017 | 30 September 2022
S0603 | Stuxnet | malware--088f1d6e-0783-47c6-9923-9c79b2af43d4 | software | uses | T0874 | Hooking | attack-pattern--ab390887-afc0-4715-826d-b1b167d522ae | technique | [Stuxnet](https://attack.mitre.org/software/S0603) modifies the Import Address Tables DLLs to hook specific APIs that are used to open project files. (Citation: Nicolas Falliere, Liam O Murchu, Eric Chien February 2011) | relationship--53a54e4a-2b38-4b0c-8f60-252a68767443 | 14 December 2017 | 20 September 2022
S0603 | Stuxnet | malware--088f1d6e-0783-47c6-9923-9c79b2af43d4 | software | uses | T0877 | I/O Image | attack-pattern--53a48c74-0025-45f4-b04a-baa853df8204 | technique | [Stuxnet](https://attack.mitre.org/software/S0603) copies the input area of an I/O image into data blocks with a one second interval between copies, forming a 21 second recording of the input area. The input area contains information being passed to the PLC from a peripheral. For example, the current state of a valve or the temperature of a device. (Citation: Nicolas Falliere, Liam O Murchu, Eric Chien February 2011) | relationship--28afd84d-a53e-4b2f-9bee-133f7da6982a | 14 December 2017 | 20 September 2022
S0603 | Stuxnet | malware--088f1d6e-0783-47c6-9923-9c79b2af43d4 | software | uses | T0867 | Lateral Tool Transfer | attack-pattern--ead7bd34-186e-4c79-9a4d-b65bcce6ed9d | technique | [Stuxnet](https://attack.mitre.org/software/S0603) sends an SQL statement that creates a table and inserts a binary value into the table. The binary value is a hex string representation of the main Stuxnet DLL as an executable file (formed using resource 210) and an updated configuration data block. (Citation: Nicolas Falliere, Liam O Murchu, Eric Chien February 2011) | relationship--327916f7-fe5d-4858-adeb-f72f74c60c25 | 08 October 2021 | 20 September 2022
S0603 | Stuxnet | malware--088f1d6e-0783-47c6-9923-9c79b2af43d4 | software | uses | T0835 | Manipulate I/O Image | attack-pattern--36e9f5bc-ac13-4da4-a2f4-01f4877d9004 | technique | When the peripheral output is written to, sequence C intercepts the output and ensures it is not written to the process image output. The output is the instructions the PLC sends to a device to change its operating behavior. By intercepting the peripheral output, [Stuxnet](https://attack.mitre.org/software/S0603) prevents an operator from noticing unauthorized commands sent to the peripheral. (Citation: Nicolas Falliere, Liam O Murchu, Eric Chien February 2011) | relationship--f0c81c9f-2fb7-4e7d-98ed-c75e3be7d962 | 14 December 2017 | 20 September 2022
S0603 | Stuxnet | malware--088f1d6e-0783-47c6-9923-9c79b2af43d4 | software | uses | T0831 | Manipulation of Control | attack-pattern--1af9e3fd-2bcc-414d-adbd-fe3b95c02ca1 | technique | [Stuxnet](https://attack.mitre.org/software/S0603) can reprogram a PLC and change critical parameters in such a way that legitimate commands can be overridden or intercepted. In addition, Stuxnet can apply inappropriate command sequences or parameters to cause damage to property. (Citation: Nicolas Falliere, Liam O Murchu, Eric Chien February 2011) | relationship--c6520346-fe47-44ce-af75-d99004ac2977 | 14 December 2017 | 20 September 2022
S0603 | Stuxnet | malware--088f1d6e-0783-47c6-9923-9c79b2af43d4 | software | uses | T0832 | Manipulation of View | attack-pattern--4c2e1408-9d68-4187-8e6b-a77bc52700ec | technique | [Stuxnet](https://attack.mitre.org/software/S0603) manipulates the view of operators replaying process input and manipulating the I/O image to evade detection and inhibit protection functions. (Citation: Langer Stuxnet) (Citation: Nicolas Falliere, Liam O Murchu, Eric Chien February 2011) | relationship--e257913e-40ba-4a05-ba97-0c3175c966b5 | 14 December 2017 | 17 March 2023
S0603 | Stuxnet | malware--088f1d6e-0783-47c6-9923-9c79b2af43d4 | software | uses | T0849 | Masquerading | attack-pattern--ba203963-3182-41ac-af14-7e7ebc83cd61 | technique | [Stuxnet](https://attack.mitre.org/software/S0603) renames s7otbxdx.dll, a dll responsible for handling communications with a PLC. It replaces this dll file with its own version that allows it to intercept any calls that are made to access the PLC. (Citation: Nicolas Falliere, Liam O Murchu, Eric Chien February 2011) | relationship--0e29f62d-4ffc-47ec-9623-72f874fbe905 | 14 December 2017 | 20 September 2022
S0603 | Stuxnet | malware--088f1d6e-0783-47c6-9923-9c79b2af43d4 | software | uses | T0821 | Modify Controller Tasking | attack-pattern--09a61657-46e1-439e-b3ed-3e4556a78243 | technique | [Stuxnet](https://attack.mitre.org/software/S0603) infects OB1 so that its malicious code sequence is executed at the start of a cycle. It also infects OB35. OB35 acts as a watchdog, and on certain conditions, it can stop the execution of OB1. (Citation: Nicolas Falliere, Liam O Murchu, Eric Chien February 2011) | relationship--ccae6e5d-8a9e-4bab-ae77-26a2bd722f67 | 13 April 2021 | 20 September 2022
S0603 | Stuxnet | malware--088f1d6e-0783-47c6-9923-9c79b2af43d4 | software | uses | T0836 | Modify Parameter | attack-pattern--097924ce-a9a9-4039-8591-e0deedfb8722 | technique | In states 3 and 4 [Stuxnet](https://attack.mitre.org/software/S0603) sends two network bursts (done through the DP_SEND primitive). The data in the frames are instructions for the frequency converter drives. For example one of the frames contains records that change the maximum frequency (the speed at which the motor will operate). The frequency converter drives consist of parameters, which can be remotely configured via Profibus. One can write new values to these parameters changing the behavior of the device. (Citation: Nicolas Falliere, Liam O Murchu, Eric Chien February 2011) | relationship--50b3247a-ea71-455e-b299-f00666c05146 | 14 December 2017 | 20 September 2022
S0603 | Stuxnet | malware--088f1d6e-0783-47c6-9923-9c79b2af43d4 | software | uses | T0889 | Modify Program | attack-pattern--fc5fda7e-6b2c-4457-b036-759896a2efa2 | technique | [Stuxnet](https://attack.mitre.org/software/S0603) infects PLCs with different code depending on the characteristics of the target system. An infection sequence consists of code blocks and data blocks that will be downloaded to the PLC to alter its behavior. (Citation: Nicolas Falliere, Liam O Murchu, Eric Chien February 2011) | relationship--cb38425c-646d-4bc8-bdea-e6cc630c3034 | 13 April 2021 | 20 September 2022
S0603 | Stuxnet | malware--088f1d6e-0783-47c6-9923-9c79b2af43d4 | software | uses | T0801 | Monitor Process State | attack-pattern--2d0d40ad-22fa-4cc8-b264-072557e1364b | technique | [Stuxnet](https://attack.mitre.org/software/S0603) examines fields recorded by the DP_RECV monitor to determine if the target system is in a particular state of operation. (Citation: Nicolas Falliere, Liam O Murchu, Eric Chien February 2011) | relationship--2fd13fc0-e3f0-4099-ab20-d19ba6bcd4e0 | 14 December 2017 | 20 September 2022
S0603 | Stuxnet | malware--088f1d6e-0783-47c6-9923-9c79b2af43d4 | software | uses | T0834 | Native API | attack-pattern--b52870cc-83f3-473c-b895-72d91751030b | technique | [Stuxnet](https://attack.mitre.org/software/S0603) calls system function blocks which are part of the operating system running on the PLC. Theyre used to execute system tasks, such as reading the system clock (SFC1) and generating data blocks on the fly. (Citation: Nicolas Falliere, Liam O Murchu, Eric Chien February 2011) | relationship--3d005ed8-77d3-4fed-9dd5-7e39ba8cb50a | 13 April 2021 | 20 September 2022
S0603 | Stuxnet | malware--088f1d6e-0783-47c6-9923-9c79b2af43d4 | software | uses | T0842 | Network Sniffing | attack-pattern--38213338-1aab-479d-949b-c81b66ccca5c | technique | DP_RECV is the name of a standard function block used by network coprocessors. It is used to receive network frames on the Profibus a standard industrial network bus used for distributed I/O. The original block is copied to FC1869, and then replaced by a malicious block. Each time the function is used to receive a packet, the malicious [Stuxnet](https://attack.mitre.org/software/S0603) block takes control: it will call the original DP_RECV in FC1869 and then perform postprocessing on the packet data. The replaced DP_RECV block (later on referred to as the DP_RECV monitor) is meant to monitor data sent by the frequency converter drives to the 315-2 CPU via CP 342-5 Profibus communication modules. (Citation: Nicolas Falliere, Liam O Murchu, Eric Chien February 2011) | relationship--f29ecf69-1753-44bb-9b80-1025f49cadda | 14 December 2017 | 20 September 2022
S0603 | Stuxnet | malware--088f1d6e-0783-47c6-9923-9c79b2af43d4 | software | uses | T0843 | Program Download | attack-pattern--be69c571-d746-4b1f-bdd0-c0c9817e9068 | technique | [Stuxnet](https://attack.mitre.org/software/S0603)'s infection sequence consists of code blocks and data blocks that will be downloaded to the PLC to alter its behavior. (Citation: Nicolas Falliere, Liam O Murchu, Eric Chien February 2011) | relationship--7c893581-c847-495a-aa93-9d98c516e1ae | 14 December 2017 | 20 September 2022
S0603 | Stuxnet | malware--088f1d6e-0783-47c6-9923-9c79b2af43d4 | software | uses | T0873 | Project File Infection | attack-pattern--e72425f8-9ae6-41d3-bfdb-e1b865e60722 | technique | [Stuxnet](https://attack.mitre.org/software/S0603) copies itself into Step 7 projects in such a way that it automatically executes when the Step 7 project is loaded. (Citation: Nicolas Falliere, Liam O Murchu, Eric Chien February 2011) | relationship--dfe43fa1-ffc2-4c6c-a91d-f2ca55f21ccb | 14 December 2017 | 12 October 2022
S0603 | Stuxnet | malware--088f1d6e-0783-47c6-9923-9c79b2af43d4 | software | uses | T0886 | Remote Services | attack-pattern--e1f9cdd2-9511-4fca-90d7-f3e92cfdd0bf | technique | [Stuxnet](https://attack.mitre.org/software/S0603) executes malicious SQL commands in the WinCC database server to propagate to remote systems. The malicious SQL commands include xp_cmdshell, sp_dumpdbilog, and sp_addextendedproc. (Citation: Nicolas Falliere, Liam O Murchu, Eric Chien February 2011) | relationship--eaeb3c8d-9d91-4eb0-8049-5cb99e141026 | 08 October 2021 | 20 September 2022
S0603 | Stuxnet | malware--088f1d6e-0783-47c6-9923-9c79b2af43d4 | software | uses | T0888 | Remote System Information Discovery | attack-pattern--2fedbe69-581f-447d-8a78-32ee7db939a9 | technique | [Stuxnet](https://attack.mitre.org/software/S0603) enumerates and parses the System Data Blocks (SDB) using the s7blk_findfirst and s7blk_findnext API calls in s7otbxdx.dll. Stuxnet must find an SDB with the DWORD at offset 50h equal to 0100CB2Ch. This specifies that the system uses the Profibus communications processor module CP 342-5. In addition, specific values are searched for and counted: 7050h and 9500h. 7050h is assigned to part number KFC750V3 which appears to be a frequency converter drive (also known as variable frequency drive) manufactured by Fararo Paya in Teheran, Iran. 9500h is assigned to Vacon NX frequency converter drives manufactured by Vacon based in Finland.(Citation: Nicolas Falliere, Liam O Murchu, Eric Chien February 2011) [Stuxnet](https://attack.mitre.org/software/S0603) was specifically targeting CPUs 6ES7-315-2 (Series 300) with special system data block characteristics for sequence A or B and 6ES7-315-2 for sequence C. The PLC type can also be checked using the s7ag_read_szl API.(Citation: Nicolas Falliere, Liam O Murchu, Eric Chien February 2011) | relationship--1d35c947-447f-4693-9ab0-32dff56e664e | 13 April 2021 | 29 September 2022
S0603 | Stuxnet | malware--088f1d6e-0783-47c6-9923-9c79b2af43d4 | software | uses | T0847 | Replication Through Removable Media | attack-pattern--c267bbee-bb59-47fe-85e0-3ed210337c21 | technique | [Stuxnet](https://attack.mitre.org/software/S0603) was able to self-replicate by being spread through removable drives. A willing insider or unknown third party, such as a contractor, may have brought the removable media into the target environment. (Citation: Nicolas Falliere, Liam O Murchu, Eric Chien February 2011) The earliest version of Stuxnet relied on physical installation, infecting target systems when an infected configuration file carried by a USB stick was opened. (Citation: Langer Stuxnet) | relationship--82b20c35-88c6-49aa-8241-a59512b17b74 | 14 December 2017 | 17 March 2023
S0603 | Stuxnet | malware--088f1d6e-0783-47c6-9923-9c79b2af43d4 | software | uses | T0851 | Rootkit | attack-pattern--3b6b9246-43f8-4c69-ad7a-2b11cfe0a0d9 | technique | One of [Stuxnet](https://attack.mitre.org/software/S0603)'s rootkits is contained entirely in the fake s7otbxdx.dll. In order to continue existing undetected on the PLC it needs to account for at least the following situations: read requests for its own malicious code blocks, read requests for infected blocks (OB1, OB35, DP_RECV), and write requests that could overwrite Stuxnets own code. Stuxnet contains code to monitor and intercept these types of requests. The rootkit modifies these requests so that Stuxnets PLC code is not discovered or damaged. (Citation: Langer Stuxnet) | relationship--f130282b-f681-455f-966b-55829842be92 | 14 December 2017 | 17 March 2023
S0603 | Stuxnet | malware--088f1d6e-0783-47c6-9923-9c79b2af43d4 | software | uses | T0869 | Standard Application Layer Protocol | attack-pattern--e076cca8-2f08-45c9-aff7-ea5ac798b387 | technique | [Stuxnet](https://attack.mitre.org/software/S0603) uses a thread to monitor a data block DB890 of sequence A or B. This thread is constantly running and probing this block (every 5 minutes). On an infected PLC, if block DB890 is found and contains a special magic value (used by Stuxnet to identify his own block DB890), this blocks data can be read and written. This thread is likely used to optimize the way sequences A and B work, and modify their behavior when the Step7 editor is opened. (Citation: Nicolas Falliere, Liam O Murchu, Eric Chien February 2011) | relationship--bc383819-2e40-49b4-bea9-95eb5d418877 | 14 December 2017 | 20 September 2022
S0603 | Stuxnet | malware--088f1d6e-0783-47c6-9923-9c79b2af43d4 | software | uses | T0863 | User Execution | attack-pattern--2736b752-4ec5-4421-a230-8977dea7649c | technique | [Stuxnet](https://attack.mitre.org/software/S0603) infects DLL's associated with the WinCC Simatic manager which are responsible for opening project files. If a user opens an uninfected project file using a compromised manager, the file will be infected with Stuxnet code. If an infected project is opened with the Simatic manager, the modified data file will trigger a search for the `xyz.dll` file. If the `xyz.dll` file is not found in any of the specified locations, the malicious DLL will be loaded and executed by the manager. (Citation: Nicolas Falliere, Liam O Murchu, Eric Chien February 2011) | relationship--8a06c15b-b7e5-4374-9265-8d9020e126cd | 14 October 2021 | 19 October 2022
S1009 | Triton | malware--80099a91-4c86-4bea-9ccb-dac55d61960e | software | uses | T0858 | Change Operating Mode | attack-pattern--2883c520-7957-46ca-89bd-dab1ad53b601 | technique | [Triton](https://attack.mitre.org/software/S1009) has the ability to halt or run a program through the TriStation protocol. TsHi.py contains instances of halt and run functions being executed. (Citation: MDudek-ICS) | relationship--74b66248-2cb6-46ea-b52c-c7d60c170f3f | 18 April 2018 | 12 October 2022
S1009 | Triton | malware--80099a91-4c86-4bea-9ccb-dac55d61960e | software | uses | T0885 | Commonly Used Port | attack-pattern--e6c31185-8040-4267-83d3-b217b8a92f07 | technique | [Triton](https://attack.mitre.org/software/S1009) uses TriStations default UDP port, 1502, to communicate with devices. (Citation: MDudek-ICS) | relationship--8b2d82aa-75fc-4d6d-bb4b-9f600bd211fd | 18 April 2018 | 12 October 2022
S1009 | Triton | malware--80099a91-4c86-4bea-9ccb-dac55d61960e | software | uses | T0868 | Detect Operating Mode | attack-pattern--2aa406ed-81c3-4c1d-ba83-cfbee5a2847a | technique | [Triton](https://attack.mitre.org/software/S1009) contains a file named TS_cnames.py which contains default definitions for program state (TS_progstate). Program state is referenced in TsHi.py.(Citation: MDudek-ICS) [Triton](https://attack.mitre.org/software/S1009) contains a file named TS_cnames.py which contains default definitions for key state (TS_keystate). Key state is referenced in TsHi.py.(Citation: MDudek-ICS) | relationship--9db1ecfe-72eb-42da-a09e-746663a53854 | 18 April 2018 | 29 September 2022
S1009 | Triton | malware--80099a91-4c86-4bea-9ccb-dac55d61960e | software | uses | T0871 | Execution through API | attack-pattern--5a2610f6-9fff-41e1-bc27-575ca20383d4 | technique | [Triton](https://attack.mitre.org/software/S1009) leverages a reconstructed TriStation protocol within its framework to trigger APIs related to program download, program allocation, and program changes. (Citation: Jos Wetzels January 2018) | relationship--d72e7d01-56be-4fbd-8957-3384533ba83b | 18 April 2018 | 12 October 2022
S1009 | Triton | malware--80099a91-4c86-4bea-9ccb-dac55d61960e | software | uses | T0820 | Exploitation for Evasion | attack-pattern--9f947a1c-3860-48a8-8af0-a2dfa3efde03 | technique | [Triton](https://attack.mitre.org/software/S1009) disables a firmware RAM/ROM consistency check after injects a payload (imain.bin) into the firmware memory region. (Citation: DHS CISA February 2019) (Citation: ICS-CERT December 2018) (Citation: Schneider Electric January 2018) Triconex systems include continuous means of detection including checksums for firmware and program integrity, memory and memory reference integrity, and configuration. (Citation: The Office of Nuclear Reactor Regulation) | relationship--ea50253a-3220-458b-b810-ad032f2b182f | 18 April 2018 | 12 October 2022
S1009 | Triton | malware--80099a91-4c86-4bea-9ccb-dac55d61960e | software | uses | T0890 | Exploitation for Privilege Escalation | attack-pattern--cfe68e93-ce94-4c0f-a57d-3aa72cedd618 | technique | [Triton](https://attack.mitre.org/software/S1009) leverages a previously-unknown vulnerability affecting Tricon MP3008 firmware versions 10.010.4 allows an insecurely-written system call to be exploited to achieve an arbitrary 2-byte write primitive, which is then used to gain supervisor privileges. (Citation: DHS CISA February 2019) | relationship--591620d3-5549-49db-9080-43f86a68a590 | 13 April 2021 | 12 October 2022
S1009 | Triton | malware--80099a91-4c86-4bea-9ccb-dac55d61960e | software | uses | T0874 | Hooking | attack-pattern--ab390887-afc0-4715-826d-b1b167d522ae | technique | [Triton](https://attack.mitre.org/software/S1009)'s injector, inject.bin, changes the function pointer of the 'get main processor diagnostic data' TriStation command to the address of imain.bin so that it is executed prior to the normal handler. (Citation: Jos Wetzels January 2018) | relationship--ccc67bb3-acc3-4294-81b3-4a0d972f2dd7 | 13 April 2021 | 12 October 2022
S1009 | Triton | malware--80099a91-4c86-4bea-9ccb-dac55d61960e | software | uses | T0872 | Indicator Removal on Host | attack-pattern--53a26eee-1080-4d17-9762-2027d5a1b805 | technique | [Triton](https://attack.mitre.org/software/S1009) would reset the controller to the previous state over TriStation and if this failed it would write a dummy program to memory in what was likely an attempt at anti-forensics. (Citation: Jos Wetzels January 2018) | relationship--56dcc2d7-5243-4a5d-a556-8723642e98a4 | 18 April 2018 | 12 October 2022
S1009 | Triton | malware--80099a91-4c86-4bea-9ccb-dac55d61960e | software | uses | T0880 | Loss of Safety | attack-pattern--5fa00fdd-4a55-4191-94a0-564181d7fec2 | technique | [Triton](https://attack.mitre.org/software/S1009) has the capability to reprogram the SIS logic to allow unsafe conditions to persist or reprogram the SIS to allow an unsafe state while using the DCS to create an unsafe state or hazard. (Citation: Blake Johnson, Dan Caban, Marina Krotofil, Dan Scali, Nathan Brubaker, Christopher Glyer December 2017) | relationship--d8354850-bd4c-4bd9-a585-b107f5f1398f | 18 April 2018 | 12 October 2022
S1009 | Triton | malware--80099a91-4c86-4bea-9ccb-dac55d61960e | software | uses | T0849 | Masquerading | attack-pattern--ba203963-3182-41ac-af14-7e7ebc83cd61 | technique | [Triton](https://attack.mitre.org/software/S1009)'s injector, inject.bin, masquerades as a standard compiled PowerPC program for the Tricon. (Citation: DHS CISA February 2019) [Triton](https://attack.mitre.org/software/S1009) was configured to masquerade as trilog.exe, which is the Triconex software for analyzing SIS logs.(Citation: FireEye TRITON) | relationship--350814da-5c36-42f9-8e58-8f9534e6ce0a | 18 April 2018 | 29 September 2022
S1009 | Triton | malware--80099a91-4c86-4bea-9ccb-dac55d61960e | software | uses | T0821 | Modify Controller Tasking | attack-pattern--09a61657-46e1-439e-b3ed-3e4556a78243 | technique | [Triton](https://attack.mitre.org/software/S1009)'s argument-setting and inject.bin shellcode are added to the program table on the Tricon so that they are executed by the firmware once each cycle. (Citation: DHS CISA February 2019) (Citation: Jos Wetzels January 2018) | relationship--63ca148e-12c9-4090-b51e-a8fb7a847a2a | 13 April 2021 | 12 October 2022
S1009 | Triton | malware--80099a91-4c86-4bea-9ccb-dac55d61960e | software | uses | T0834 | Native API | attack-pattern--b52870cc-83f3-473c-b895-72d91751030b | technique | [Triton](https://attack.mitre.org/software/S1009)'s imain.bin payload takes commands from the TsHi.ExplReadRam(Ex), TsHi.ExplWriteRam(Ex) and TsHi.ExplExec functions to perform operations on controller memory and registers using syscalls written in PowerPC shellcode. (Citation: Jos Wetzels January 2018) | relationship--13809e98-1d74-4c39-b882-9d523c76cbde | 13 April 2021 | 12 October 2022
S1009 | Triton | malware--80099a91-4c86-4bea-9ccb-dac55d61960e | software | uses | T0843 | Program Download | attack-pattern--be69c571-d746-4b1f-bdd0-c0c9817e9068 | technique | [Triton](https://attack.mitre.org/software/S1009) leveraged the TriStation protocol to download programs onto Triconex Safety Instrumented System. (Citation: Jos Wetzels January 2018) | relationship--1f8abf6f-0dd0-4449-b555-733fe7296177 | 18 April 2018 | 12 October 2022
S1009 | Triton | malware--80099a91-4c86-4bea-9ccb-dac55d61960e | software | uses | T0845 | Program Upload | attack-pattern--3067b85e-271e-4bc5-81ad-ab1a81d411e3 | technique | [Triton](https://attack.mitre.org/software/S1009) calls the SafeAppendProgramMod to transfer its payloads to the Tricon. Part of this call includes preforming a program upload. (Citation: MDudek-ICS) | relationship--a946c9b1-5b89-44c9-b617-3412ffda34b9 | 18 April 2018 | 12 October 2022
S1009 | Triton | malware--80099a91-4c86-4bea-9ccb-dac55d61960e | software | uses | T0846 | Remote System Discovery | attack-pattern--d5a69cfb-fc2a-46cb-99eb-74b236db5061 | technique | [Triton](https://attack.mitre.org/software/S1009) uses a Python script that is capable of detecting Triconex controllers on the network by sending a specific UDP broadcast packet over port 1502. (Citation: DHS CISA February 2019) | relationship--351e19c4-c16e-493a-9800-a433107aacf1 | 18 April 2018 | 12 October 2022
S1009 | Triton | malware--80099a91-4c86-4bea-9ccb-dac55d61960e | software | uses | T0853 | Scripting | attack-pattern--2dc2b567-8821-49f9-9045-8740f3d0b958 | technique | [Triton](https://attack.mitre.org/software/S1009) communicates with Triconex controllers using a custom component framework written entirely in Python. The modules that implement the TriStation communication protocol and other supporting components are found in a separate file -- library.zip -- the main script that employs this functionality is compiled into a standalone py2exe Windows executable -- trilog.exe which includes a Python environment. (Citation: DHS CISA February 2019) | relationship--709c4e40-c5c6-405b-bc3d-0adfea40ccd4 | 18 April 2018 | 12 October 2022
S1009 | Triton | malware--80099a91-4c86-4bea-9ccb-dac55d61960e | software | uses | T0869 | Standard Application Layer Protocol | attack-pattern--e076cca8-2f08-45c9-aff7-ea5ac798b387 | technique | [Triton](https://attack.mitre.org/software/S1009) can communicate with the implant utilizing the TriStation 'get main processor diagnostic data' command and looks for a specifically crafted packet body from which it extracts a command value and its arguments. (Citation: Jos Wetzels January 2018) | relationship--f584a257-c22a-434b-aa2d-6220987821ab | 13 October 2021 | 12 October 2022
S1009 | Triton | malware--80099a91-4c86-4bea-9ccb-dac55d61960e | software | uses | T0857 | System Firmware | attack-pattern--b9160e77-ea9e-4ba9-b1c8-53a3c466b13d | technique | [Triton](https://attack.mitre.org/software/S1009) is able to read, write and execute code in memory on the safety controller at an arbitrary address within the devices firmware region. This allows the malware to make changes to the running firmware in memory and modify how the device operates. (Citation: DHS CISA February 2019) | relationship--93e24e03-6425-4ee8-99bb-c3a662c6cdce | 18 April 2018 | 12 October 2022
S1010 | VPNFilter | malware--6108f800-10b8-4090-944e-be579f01263d | software | uses | T0830 | Adversary-in-the-Middle | attack-pattern--9a505987-ab05-4f46-a9a6-6441442eec3b | technique | The [VPNFilter](https://attack.mitre.org/software/S1010)'s ssler module configures the device's iptables to redirect all traffic destined for port 80 to its local service listening on port 8888. Any outgoing web requests on port 80 are now intercepted by ssler and can be inspected by the ps module and manipulated before being sent to the legitimate HTTP service. (Citation: William Largent June 2018) (Citation: Carl Hurd March 2019) | relationship--c84e39ab-30c1-40e3-95a8-fcbb271e913c | 06 May 2022 | 12 October 2022
S1010 | VPNFilter | malware--6108f800-10b8-4090-944e-be579f01263d | software | uses | T0842 | Network Sniffing | attack-pattern--38213338-1aab-479d-949b-c81b66ccca5c | technique | The [VPNFilter](https://attack.mitre.org/software/S1010) packet sniffer looks for basic authentication as well as monitors ICS traffic, and is specific to the TP-LINK R600-VPN. The malware uses a raw socket to look for connections to a pre-specified IP address, only looking at TCP packets that are 150 bytes or larger. Packets that are not on port 502, are scanned for BasicAuth, and that information is logged. This may have allowed credential harvesting from communications between devices accessing a modbus-enabled HMI. (Citation: William Largent June 2018) (Citation: Carl Hurd March 2019) | relationship--cad91f87-7cc7-4771-8c7b-1599793ed3c1 | 17 October 2018 | 12 October 2022
S0366 | WannaCry | malware--75ecdbf1-c2bb-4afc-a3f9-c8da4de8c661 | software | uses | T0866 | Exploitation of Remote Services | attack-pattern--85a45294-08f1-4539-bf00-7da08aa7b0ee | technique | [WannaCry](https://attack.mitre.org/software/S0366) initially infected IT networks, but by means of an exploit (particularly the SMBv1-targeting MS17-010 vulnerability) spread to industrial networks. (Citation: Joe Slowik April 2019) | relationship--c59a3d89-c8fa-4c5d-813e-f4495d892d1a | 25 March 2019 | 12 October 2022
S0366 | WannaCry | malware--75ecdbf1-c2bb-4afc-a3f9-c8da4de8c661 | software | uses | T0867 | Lateral Tool Transfer | attack-pattern--ead7bd34-186e-4c79-9a4d-b65bcce6ed9d | technique | [WannaCry](https://attack.mitre.org/software/S0366) can move laterally through industrial networks by means of the SMB service. (Citation: Joe Slowik April 2019) | relationship--d50a3d89-c8fa-4c5d-813e-f4495d892d1a | 25 March 2019 | 12 October 2022

## associated mitigations
source ID | source name | source ref | source type | mapping type | target ID | target name | target ref | target type | mapping description | STIX ID | created | last modified
M0801 | Access Management | course-of-action--3992ce42-43e9-4bea-b8db-a102ec3ec1e3 | mitigation | mitigates | T0800 | Activate Firmware Update Mode | attack-pattern--19a71d1e-6334-4233-8260-b749cae37953 | technique | All devices or systems changes, including all administrative functions, should require authentication. Consider using access management technologies to enforce authorization on all management interface access attempts, especially when the device does not inherently provide strong authentication and authorization functions. | relationship--b3b24837-83ed-46c5-ba80-66a832c7072e | 21 September 2020 | 06 May 2022
M0801 | Access Management | course-of-action--3992ce42-43e9-4bea-b8db-a102ec3ec1e3 | mitigation | mitigates | T0858 | Change Operating Mode | attack-pattern--2883c520-7957-46ca-89bd-dab1ad53b601 | technique | Authenticate all access to field controllers before authorizing access to, or modification of, a device's state, logic, or programs. Centralized authentication techniques can help manage the large number of field controller accounts needed across the ICS. | relationship--a86cee0a-dc49-4c95-b5dc-37405337490b | 21 September 2020 | 06 May 2022
M0801 | Access Management | course-of-action--3992ce42-43e9-4bea-b8db-a102ec3ec1e3 | mitigation | mitigates | T0812 | Default Credentials | attack-pattern--8bb4538f-f16f-49f0-a431-70b5444c7349 | technique | Ensure embedded controls and network devices are protected through access management, as these devices often have unknown default accounts which could be used to gain unauthorized access. | relationship--3ed98d8c-de30-499e-9a62-eae0207519f4 | 21 September 2020 | 06 May 2022
M0801 | Access Management | course-of-action--3992ce42-43e9-4bea-b8db-a102ec3ec1e3 | mitigation | mitigates | T0868 | Detect Operating Mode | attack-pattern--2aa406ed-81c3-4c1d-ba83-cfbee5a2847a | technique | Authenticate all access to field controllers before authorizing access to, or modification of, a device's state, logic, or programs. Centralized authentication techniques can help manage the large number of field controller accounts needed across the ICS. | relationship--6637d8e6-6578-4d15-a993-d63ced4c4464 | 21 September 2020 | 06 May 2022
M0801 | Access Management | course-of-action--3992ce42-43e9-4bea-b8db-a102ec3ec1e3 | mitigation | mitigates | T0816 | Device Restart/Shutdown | attack-pattern--25dfc8ad-bd73-4dfd-84a9-3c3d383f76e9 | technique | All devices or systems changes, including all administrative functions, should require authentication. Consider using access management technologies to enforce authorization on all management interface access attempts, especially when the device does not inherently provide strong authentication and authorization functions. | relationship--e8af0b34-4a67-4966-a34a-c4d1b346ea15 | 21 September 2020 | 06 May 2022
M0801 | Access Management | course-of-action--3992ce42-43e9-4bea-b8db-a102ec3ec1e3 | mitigation | mitigates | T0871 | Execution through API | attack-pattern--5a2610f6-9fff-41e1-bc27-575ca20383d4 | technique | Access Management technologies can be used to enforce authorization policies and decisions, especially when existing field devices do not provide capabilities to support user identification and authentication. (Citation: McCarthy, J et al. July 2018) These technologies typically utilize an in-line network device or gateway system to prevent access to unauthenticated users, while also integrating with an authentication service to first verify user credentials. | relationship--efb80069-e4be-4055-bd34-06d1376b4601 | 21 September 2020 | 06 May 2022
M0801 | Access Management | course-of-action--3992ce42-43e9-4bea-b8db-a102ec3ec1e3 | mitigation | mitigates | T0891 | Hardcoded Credentials | attack-pattern--c9a8d958-fcdb-40d2-af4c-461c8031651a | technique | Ensure embedded controls and network devices are protected through access management, as these devices often have unknown hardcoded accounts which could be used to gain unauthorized access. | relationship--5714c88f-ca54-46b6-b072-cd1d24714ae0 | 29 September 2022 | 29 September 2022
M0801 | Access Management | course-of-action--3992ce42-43e9-4bea-b8db-a102ec3ec1e3 | mitigation | mitigates | T0838 | Modify Alarm Settings | attack-pattern--e5de767e-f513-41cd-aa15-33f6ce5fbf92 | technique | All devices or systems changes, including all administrative functions, should require authentication. Consider using access management technologies to enforce authorization on all management interface access attempts, especially when the device does not inherently provide strong authentication and authorization functions. | relationship--f20d8eed-b517-4297-b32a-9a5e0845de9f | 21 September 2020 | 06 May 2022
M0801 | Access Management | course-of-action--3992ce42-43e9-4bea-b8db-a102ec3ec1e3 | mitigation | mitigates | T0839 | Module Firmware | attack-pattern--efbf7888-f61b-4572-9c80-7e2965c60707 | technique | All devices or systems changes, including all administrative functions, should require authentication. Consider using access management technologies to enforce authorization on all management interface access attempts, especially when the device does not inherently provide strong authentication and authorization functions. | relationship--d1971b32-3a15-4544-9f36-80c05121deb6 | 21 September 2020 | 06 May 2022
M0801 | Access Management | course-of-action--3992ce42-43e9-4bea-b8db-a102ec3ec1e3 | mitigation | mitigates | T0861 | Point & Tag Identification | attack-pattern--25852363-5968-4673-b81d-341d5ed90bd1 | technique | Authenticate all access to field controllers before authorizing access to, or modification of, a device's state, logic, or programs. Centralized authentication techniques can help manage the large number of field controller accounts needed across the ICS. | relationship--b7f23af2-e948-4531-af56-1a1b4d03702f | 21 September 2020 | 06 May 2022
M0801 | Access Management | course-of-action--3992ce42-43e9-4bea-b8db-a102ec3ec1e3 | mitigation | mitigates | T0843 | Program Download | attack-pattern--be69c571-d746-4b1f-bdd0-c0c9817e9068 | technique | Authenticate all access to field controllers before authorizing access to, or modification of, a device's state, logic, or programs. Centralized authentication techniques can help manage the large number of field controller accounts needed across the ICS. | relationship--ec105f62-2552-41fa-8b07-619dc1bf9b19 | 21 September 2020 | 06 May 2022
M0801 | Access Management | course-of-action--3992ce42-43e9-4bea-b8db-a102ec3ec1e3 | mitigation | mitigates | T0845 | Program Upload | attack-pattern--3067b85e-271e-4bc5-81ad-ab1a81d411e3 | technique | Authenticate all access to field controllers before authorizing access to, or modification of, a device's state, logic, or programs. Centralized authentication techniques can help manage the large number of field controller accounts needed across the ICS. | relationship--5ca1d677-b41f-4f1e-b86b-f5637a418829 | 21 September 2020 | 06 May 2022
M0801 | Access Management | course-of-action--3992ce42-43e9-4bea-b8db-a102ec3ec1e3 | mitigation | mitigates | T0886 | Remote Services | attack-pattern--e1f9cdd2-9511-4fca-90d7-f3e92cfdd0bf | technique | Access Management technologies can help enforce authentication on critical remote service, examples include, but are not limited to, device management services (e.g., telnet, SSH), data access servers (e.g., HTTP, Historians), and HMI sessions (e.g., RDP, VNC). | relationship--c9065f74-556d-4728-8072-f96642e70316 | 12 April 2021 | 06 May 2022
M0801 | Access Management | course-of-action--3992ce42-43e9-4bea-b8db-a102ec3ec1e3 | mitigation | mitigates | T0857 | System Firmware | attack-pattern--b9160e77-ea9e-4ba9-b1c8-53a3c466b13d | technique | All devices or systems changes, including all administrative functions, should require authentication. Consider using access management technologies to enforce authorization on all management interface access attempts, especially when the device does not inherently provide strong authentication and authorization functions. | relationship--68d30c45-766f-48b6-9405-0c969243332b | 21 September 2020 | 06 May 2022
M0801 | Access Management | course-of-action--3992ce42-43e9-4bea-b8db-a102ec3ec1e3 | mitigation | mitigates | T0859 | Valid Accounts | attack-pattern--cd2c76a4-5e23-4ca5-9c40-d5e0604f7101 | technique | Authenticate all access to field controllers before authorizing access to, or modification of, a device's state, logic, or programs. Centralized authentication techniques can help manage the large number of field controller accounts needed across the ICS. | relationship--104b4f25-d0a9-41f6-94b3-fa85ee8b1523 | 21 September 2020 | 06 May 2022
M0936 | Account Use Policies | course-of-action--86b455f2-fb63-4043-93a8-32a3a7703a02 | mitigation | mitigates | T0822 | External Remote Services | attack-pattern--8d2f3bab-507c-4424-b58b-edc977bd215c | technique | Configure features related to account use like login attempt lockouts, specific login times, and password strength requirements as examples. Consider these features as they relate to assets which may impact safety and availability. (Citation: Keith Stouffer May 2015) | relationship--276aa6a6-e700-470a-8f72-02537ba7be9d | 21 September 2020 | 06 May 2022
M0936 | Account Use Policies | course-of-action--86b455f2-fb63-4043-93a8-32a3a7703a02 | mitigation | mitigates | T0859 | Valid Accounts | attack-pattern--cd2c76a4-5e23-4ca5-9c40-d5e0604f7101 | technique | Configure features related to account use like login attempt lockouts, specific login times, and password strength requirements as examples. Consider these features as they relate to assets which may impact safety and availability. (Citation: Keith Stouffer May 2015) | relationship--ea817c7a-9424-4204-90a5-6f8fb86037be | 21 September 2020 | 06 May 2022
M0915 | Active Directory Configuration | course-of-action--2f0160b7-e982-49d7-9612-f19b810f1722 | mitigation | mitigates | T0859 | Valid Accounts | attack-pattern--cd2c76a4-5e23-4ca5-9c40-d5e0604f7101 | technique | Consider configuration and use of a network-wide authentication service such as Active Directory, LDAP, or RADIUS capabilities which can be found in ICS devices. (Citation: Keith Stouffer May 2015) (Citation: Schweitzer Engineering Laboratories August 2015) | relationship--eeeaa0d4-0ca0-468e-ae13-43ab7aba61b4 | 21 September 2020 | 06 May 2022
M0949 | Antivirus/Antimalware | course-of-action--faf2b40e-5981-433f-aa46-17458e0026f7 | mitigation | mitigates | T0865 | Spearphishing Attachment | attack-pattern--648f995e-9c3a-41e4-aeee-98bb41037426 | technique | Deploy anti-virus on all systems that support external email. | relationship--bda03e8d-5e06-4470-b786-11b11c7c97c7 | 21 September 2020 | 06 May 2022
M0949 | Antivirus/Antimalware | course-of-action--faf2b40e-5981-433f-aa46-17458e0026f7 | mitigation | mitigates | T0864 | Transient Cyber Asset | attack-pattern--35392fb4-a31d-4c6a-b9f2-1c65b7f5e6b9 | technique | Install anti-virus software on all workstation and transient assets that may have external access, such as to web, email, or remote file shares. | relationship--6c15ec9f-2b48-419c-adc1-f989833f6187 | 14 October 2021 | 06 May 2022
M0949 | Antivirus/Antimalware | course-of-action--faf2b40e-5981-433f-aa46-17458e0026f7 | mitigation | mitigates | T0863 | User Execution | attack-pattern--2736b752-4ec5-4421-a230-8977dea7649c | technique | Ensure anti-virus solution can detect malicious files that allow user execution (e.g., Microsoft Office Macros, program installers). | relationship--d3c94120-e6b5-4bd2-88f0-9c73f76b0104 | 21 September 2020 | 06 May 2022
M0913 | Application Developer Guidance | course-of-action--8a3aadd0-b5f4-433a-800e-4893e4196bb7 | mitigation | mitigates | T0859 | Valid Accounts | attack-pattern--cd2c76a4-5e23-4ca5-9c40-d5e0604f7101 | technique | Ensure that applications and devices do not store sensitive data or credentials insecurely (e.g., plaintext credentials in code, published credentials in repositories, or credentials in public cloud storage). (Citation: CISA June 2013) | relationship--b69f31c3-6c12-4b81-8e74-9c58ea635fa4 | 21 September 2020 | 06 May 2022
M0948 | Application Isolation and Sandboxing | course-of-action--059ba11e-e3dc-49aa-84ca-88197f40d4ea | mitigation | mitigates | T0817 | Drive-by Compromise | attack-pattern--7830cfcf-b268-4ac0-a69e-73c6affbae9a | technique | Built-in browser sandboxes and application isolation may be used to contain web-based malware. | relationship--ca5c7ae7-5273-4888-bc50-183d6e200972 | 21 September 2020 | 06 May 2022
M0948 | Application Isolation and Sandboxing | course-of-action--059ba11e-e3dc-49aa-84ca-88197f40d4ea | mitigation | mitigates | T0819 | Exploit Public-Facing Application | attack-pattern--32632a95-6856-47b9-9ab7-fea5cd7dce00 | technique | Application isolation will limit the other processes and system features an exploited target can access. Examples of built in features are software restriction policies, AppLocker for Windows, and SELinux or AppArmor for Linux. | relationship--e767c178-e4b2-490a-b544-bb1b2d6c7de4 | 21 September 2020 | 06 May 2022
M0948 | Application Isolation and Sandboxing | course-of-action--059ba11e-e3dc-49aa-84ca-88197f40d4ea | mitigation | mitigates | T0820 | Exploitation for Evasion | attack-pattern--9f947a1c-3860-48a8-8af0-a2dfa3efde03 | technique | Make it difficult for adversaries to advance their operation through exploitation of undiscovered or unpatched vulnerabilities by using sandboxing. Other types of virtualization and application microsegmentation may also mitigate the impact of some types of exploitation. Risks of additional exploits and weaknesses in these systems may still exist. (Citation: Dan Goodin March 2017) | relationship--7ff12adb-bc9a-42e5-9cbf-613b200c36dc | 21 September 2020 | 06 May 2022
M0948 | Application Isolation and Sandboxing | course-of-action--059ba11e-e3dc-49aa-84ca-88197f40d4ea | mitigation | mitigates | T0890 | Exploitation for Privilege Escalation | attack-pattern--cfe68e93-ce94-4c0f-a57d-3aa72cedd618 | technique | Make it difficult for adversaries to advance their operation through exploitation of undiscovered or unpatched vulnerabilities by using sandboxing. Other types of virtualization and application microsegmentation may also mitigate the impact of some types of exploitation. Risks of additional exploits and weaknesses in these systems may still exist. (Citation: Dan Goodin March 2017) | relationship--5f03ee5d-534c-454c-aae3-b41130b00286 | 13 April 2021 | 06 May 2022
M0948 | Application Isolation and Sandboxing | course-of-action--059ba11e-e3dc-49aa-84ca-88197f40d4ea | mitigation | mitigates | T0866 | Exploitation of Remote Services | attack-pattern--85a45294-08f1-4539-bf00-7da08aa7b0ee | technique | Make it difficult for adversaries to advance their operation through exploitation of undiscovered or unpatched vulnerabilities by using sandboxing. Other types of virtualization and application microsegmentation may also mitigate the impact of some types of exploitation. Risks of additional exploits and weaknesses in these systems may still exist. (Citation: Dan Goodin March 2017) | relationship--8fa6fe89-e704-4be4-a15b-50e188084aa3 | 21 September 2020 | 06 May 2022
M0948 | Application Isolation and Sandboxing | course-of-action--059ba11e-e3dc-49aa-84ca-88197f40d4ea | mitigation | mitigates | T0853 | Scripting | attack-pattern--2dc2b567-8821-49f9-9045-8740f3d0b958 | technique | Consider the use of application isolation and sandboxing to restrict specific operating system interactions such as access through user accounts, services, system calls, registry, and network access. This may be even more useful in cases where the source of the executed script is unknown. | relationship--2fffbea8-c031-4de8-a451-447bbbe3e224 | 21 September 2020 | 06 May 2022
M0947 | Audit | course-of-action--bcf91ebc-f316-4e19-b2f6-444e9940c697 | mitigation | mitigates | T0830 | Adversary-in-the-Middle | attack-pattern--9a505987-ab05-4f46-a9a6-6441442eec3b | technique | Limit access to network infrastructure and resources that can be used to reshape traffic or otherwise produce AiTM conditions. | relationship--b47dbc50-fd8f-4e5b-bb3d-e93b68bf5497 | 21 September 2020 | 21 March 2023
M0947 | Audit | course-of-action--bcf91ebc-f316-4e19-b2f6-444e9940c697 | mitigation | mitigates | T0811 | Data from Information Repositories | attack-pattern--3405891b-16aa-4bd7-bd7c-733501f9b20f | technique | Consider periodic reviews of accounts and privileges for critical and sensitive repositories. | relationship--2ff82993-5010-4450-89e7-341f449f3263 | 21 September 2020 | 06 May 2022
M0947 | Audit | course-of-action--bcf91ebc-f316-4e19-b2f6-444e9940c697 | mitigation | mitigates | T0874 | Hooking | attack-pattern--ab390887-afc0-4715-826d-b1b167d522ae | technique | Perform audits or scans of systems, permissions, insecure software, insecure configurations, etc. to identify potential weaknesses. Perform periodic integrity checks of the device to validate the correctness of the firmware, software, programs, and configurations. Integrity checks, which typically include cryptographic hashes or digital signatures, should be compared to those obtained at known valid states, especially after events like device reboots, program downloads, or program restarts. | relationship--b72b7dfd-f134-4324-84b8-52ff13fc6b5c | 21 September 2020 | 06 May 2022
M0947 | Audit | course-of-action--bcf91ebc-f316-4e19-b2f6-444e9940c697 | mitigation | mitigates | T0821 | Modify Controller Tasking | attack-pattern--09a61657-46e1-439e-b3ed-3e4556a78243 | technique | Provide the ability to verify the integrity of controller tasking. While techniques like CRCs and checksums are commonly used, they are not cryptographically secure and can be vulnerable to collisions. Preferably cryptographic hash functions (e.g., SHA-2, SHA-3) should be used. (Citation: IEC February 2019) | relationship--698d7c50-daab-4087-a7b4-b2bc8dfd81a7 | 13 April 2021 | 25 September 2023
M0947 | Audit | course-of-action--bcf91ebc-f316-4e19-b2f6-444e9940c697 | mitigation | mitigates | T0836 | Modify Parameter | attack-pattern--097924ce-a9a9-4039-8591-e0deedfb8722 | technique | Provide the ability to verify the integrity and authenticity of changes to parameter values. | relationship--5bf8473c-3c60-4a8a-8514-c2b50ab8a92d | 21 September 2020 | 25 September 2023
M0947 | Audit | course-of-action--bcf91ebc-f316-4e19-b2f6-444e9940c697 | mitigation | mitigates | T0889 | Modify Program | attack-pattern--fc5fda7e-6b2c-4457-b036-759896a2efa2 | technique | Provide the ability to verify the integrity of control logic or programs loaded on a controller. While techniques like CRCs and checksums are commonly used, they are not cryptographically strong and can be vulnerable to collisions. Preferably cryptographic hash functions (e.g., SHA-2, SHA-3) should be used. (Citation: IEC February 2019) | relationship--34ac1b1b-1103-4fc9-a62e-f1dd1451b28b | 13 April 2021 | 06 May 2022
M0947 | Audit | course-of-action--bcf91ebc-f316-4e19-b2f6-444e9940c697 | mitigation | mitigates | T0839 | Module Firmware | attack-pattern--efbf7888-f61b-4572-9c80-7e2965c60707 | technique | Perform integrity checks of firmware before uploading it on a device. Utilize cryptographic hashes to verify the firmware has not been tampered with by comparing it to a trusted hash of the firmware. This could be from trusted data sources (e.g., vendor site) or through a third-party verification service. | relationship--65a45501-10de-46a2-89bf-03bbf17aba33 | 21 September 2020 | 06 May 2022
M0947 | Audit | course-of-action--bcf91ebc-f316-4e19-b2f6-444e9940c697 | mitigation | mitigates | T0843 | Program Download | attack-pattern--be69c571-d746-4b1f-bdd0-c0c9817e9068 | technique | Provide the ability to verify the integrity of programs downloaded on a controller. While techniques like CRCs and checksums are commonly used, they are not cryptographically secure and can be vulnerable to collisions. Preferably cryptographic hash functions (e.g., SHA-2, SHA-3) should be used. (Citation: IEC February 2019) | relationship--1c3d966a-5995-48ed-919d-25b972010fe9 | 21 September 2020 | 25 September 2023
M0947 | Audit | course-of-action--bcf91ebc-f316-4e19-b2f6-444e9940c697 | mitigation | mitigates | T0873 | Project File Infection | attack-pattern--e72425f8-9ae6-41d3-bfdb-e1b865e60722 | technique | Review the integrity of project files to verify they have not been modified by adversary behavior. Verify a cryptographic hash for the file with a known trusted version, or look for other indicators of modification (e.g., timestamps). | relationship--f9aa3364-a1eb-4776-ae03-c39b250545a0 | 21 September 2020 | 06 May 2022
M0947 | Audit | course-of-action--bcf91ebc-f316-4e19-b2f6-444e9940c697 | mitigation | mitigates | T0851 | Rootkit | attack-pattern--3b6b9246-43f8-4c69-ad7a-2b11cfe0a0d9 | technique | Audit the integrity of PLC system and application code functionality, such as the manipulation of standard function blocks (e.g., Organizational Blocks) that manage the execution of application logic programs. (Citation: IEC February 2019) | relationship--5de6bf53-0a02-439b-a8d0-248fa9640a36 | 21 September 2020 | 06 May 2022
M0947 | Audit | course-of-action--bcf91ebc-f316-4e19-b2f6-444e9940c697 | mitigation | mitigates | T0862 | Supply Chain Compromise | attack-pattern--5e0f75da-e108-4688-a6de-a4f07cc2cbe3 | technique | Perform audits or scans of systems, permissions, insecure software, insecure configurations, etc. to identify potential weaknesses. Perform periodic integrity checks of the device to validate the correctness of the firmware, software, programs, and configurations. Integrity checks, which typically include cryptographic hashes or digital signatures, should be compared to those obtained at known valid states, especially after events like device reboots, program downloads, or program restarts. | relationship--0491ef92-2941-4841-9fe6-2e1809788b52 | 21 September 2020 | 06 May 2022
M0947 | Audit | course-of-action--bcf91ebc-f316-4e19-b2f6-444e9940c697 | mitigation | mitigates | T0857 | System Firmware | attack-pattern--b9160e77-ea9e-4ba9-b1c8-53a3c466b13d | technique | Perform integrity checks of firmware before uploading it on a device. Utilize cryptographic hashes to verify the firmware has not been tampered with by comparing it to a trusted hash of the firmware. This could be from trusted data sources (e.g., vendor site) or through a third-party verification service. | relationship--04fa6b94-d633-40ff-9ab2-88f58c07c3e1 | 21 September 2020 | 06 May 2022
M0947 | Audit | course-of-action--bcf91ebc-f316-4e19-b2f6-444e9940c697 | mitigation | mitigates | T0864 | Transient Cyber Asset | attack-pattern--35392fb4-a31d-4c6a-b9f2-1c65b7f5e6b9 | technique | Integrity checking of transient assets can include performing the validation of the booted operating system and programs using TPM-based technologies, such as Secure Boot and Trusted Boot. (Citation: Emerson Exchange) It can also include verifying filesystem changes, such as programs and configuration files stored on the system, executing processes, libraries, accounts, and open ports. (Citation: National Security Agency February 2016) | relationship--5041e17d-6349-4589-8c61-7b43964b5f9b | 14 October 2021 | 06 May 2022
M0947 | Audit | course-of-action--bcf91ebc-f316-4e19-b2f6-444e9940c697 | mitigation | mitigates | T0859 | Valid Accounts | attack-pattern--cd2c76a4-5e23-4ca5-9c40-d5e0604f7101 | technique | Routinely audit source code, application configuration files, open repositories, and public cloud storage for insecure use and storage of credentials. | relationship--baf7daf3-2116-4051-91b5-f82e146167d0 | 21 September 2020 | 06 May 2022
M0800 | Authorization Enforcement | course-of-action--e0d38502-decb-481d-ad8b-b8f0a0c330bd | mitigation | mitigates | T0800 | Activate Firmware Update Mode | attack-pattern--19a71d1e-6334-4233-8260-b749cae37953 | technique | Restrict configurations changes and firmware updating abilities to only authorized individuals. | relationship--ff3f0668-98df-44c1-88c2-711f05720eb8 | 21 September 2020 | 06 May 2022
M0800 | Authorization Enforcement | course-of-action--e0d38502-decb-481d-ad8b-b8f0a0c330bd | mitigation | mitigates | T0858 | Change Operating Mode | attack-pattern--2883c520-7957-46ca-89bd-dab1ad53b601 | technique | All field controllers should restrict operating mode changes to only required authenticated users (e.g., engineers, field technicians), preferably through implementing a role-based access mechanism. Further, physical mechanisms (e.g., keys) can also be used to limit unauthorized operating mode changes. | relationship--eeeff03f-7436-4f76-8591-42075e6647d4 | 21 September 2020 | 06 May 2022
M0800 | Authorization Enforcement | course-of-action--e0d38502-decb-481d-ad8b-b8f0a0c330bd | mitigation | mitigates | T0868 | Detect Operating Mode | attack-pattern--2aa406ed-81c3-4c1d-ba83-cfbee5a2847a | technique | All field controllers should restrict the modification of programs to only certain users (e.g., engineers, field technician), preferably through implementing a role-based access mechanism. | relationship--b8f6d6a8-e668-4596-8ec2-41c5d1bd211d | 21 September 2020 | 06 May 2022
M0800 | Authorization Enforcement | course-of-action--e0d38502-decb-481d-ad8b-b8f0a0c330bd | mitigation | mitigates | T0816 | Device Restart/Shutdown | attack-pattern--25dfc8ad-bd73-4dfd-84a9-3c3d383f76e9 | technique | All field controllers should restrict the modification of programs to only certain users (e.g., engineers, field technician), preferably through implementing a role-based access mechanism. | relationship--6b5fd6d8-ef70-4896-b1a4-7b6c29c3a0d4 | 21 September 2020 | 06 May 2022
M0800 | Authorization Enforcement | course-of-action--e0d38502-decb-481d-ad8b-b8f0a0c330bd | mitigation | mitigates | T0871 | Execution through API | attack-pattern--5a2610f6-9fff-41e1-bc27-575ca20383d4 | technique | All APIs used to perform execution, especially those hosted on embedded controllers (e.g., PLCs), should provide adequate authorization enforcement of user access. Minimize user's access to only required API calls. (Citation: MITRE June 2020) | relationship--754521fc-4306-4daa-831b-6b6fb45847e2 | 21 September 2020 | 06 May 2022
M0800 | Authorization Enforcement | course-of-action--e0d38502-decb-481d-ad8b-b8f0a0c330bd | mitigation | mitigates | T0838 | Modify Alarm Settings | attack-pattern--e5de767e-f513-41cd-aa15-33f6ce5fbf92 | technique | Only authorized personnel should be able to change settings for alarms. | relationship--6b5d2643-b399-43aa-8ab1-7557a0446b07 | 21 September 2020 | 06 May 2022
M0800 | Authorization Enforcement | course-of-action--e0d38502-decb-481d-ad8b-b8f0a0c330bd | mitigation | mitigates | T0821 | Modify Controller Tasking | attack-pattern--09a61657-46e1-439e-b3ed-3e4556a78243 | technique | All field controllers should restrict the modification of controller tasks to only certain users (e.g., engineers, field technician), preferably through implementing a role-based access mechanism. | relationship--4653847b-c089-4435-9159-6f76353833f7 | 25 September 2023 | 25 September 2023
M0800 | Authorization Enforcement | course-of-action--e0d38502-decb-481d-ad8b-b8f0a0c330bd | mitigation | mitigates | T0836 | Modify Parameter | attack-pattern--097924ce-a9a9-4039-8591-e0deedfb8722 | technique | All field controllers should restrict the modification of parameter values to only certain users (e.g., engineers, field technician), preferably through implementing a role-based access mechanism. They should also restrict online edits and enable write protection for parameters. | relationship--e6be2fb4-3815-4e52-8dec-2aed1dc3b7cf | 21 September 2020 | 25 September 2023
M0800 | Authorization Enforcement | course-of-action--e0d38502-decb-481d-ad8b-b8f0a0c330bd | mitigation | mitigates | T0889 | Modify Program | attack-pattern--fc5fda7e-6b2c-4457-b036-759896a2efa2 | technique | All field controllers should restrict the modification of programs to only certain users (e.g., engineers, field technician), preferably through implementing a role-based access mechanism. | relationship--d2a434c7-4428-435e-ae6b-e54012f29606 | 25 September 2023 | 25 September 2023
M0800 | Authorization Enforcement | course-of-action--e0d38502-decb-481d-ad8b-b8f0a0c330bd | mitigation | mitigates | T0861 | Point & Tag Identification | attack-pattern--25852363-5968-4673-b81d-341d5ed90bd1 | technique | Systems and devices should restrict access to any data with potential confidentiality concerns, including point and tag information. | relationship--243ad7b2-546c-4bf2-a3c0-1438b13e197d | 21 September 2020 | 06 May 2022
M0800 | Authorization Enforcement | course-of-action--e0d38502-decb-481d-ad8b-b8f0a0c330bd | mitigation | mitigates | T0843 | Program Download | attack-pattern--be69c571-d746-4b1f-bdd0-c0c9817e9068 | technique | All field controllers should restrict the download of programs, including online edits and program appends, to only certain users (e.g., engineers, field technician), preferably through implementing a role-based access mechanism. | relationship--a7caa7f2-cfb9-4fc9-ae8d-49349b6c260f | 21 September 2020 | 25 September 2023
M0800 | Authorization Enforcement | course-of-action--e0d38502-decb-481d-ad8b-b8f0a0c330bd | mitigation | mitigates | T0845 | Program Upload | attack-pattern--3067b85e-271e-4bc5-81ad-ab1a81d411e3 | technique | All field controllers should restrict program uploads to only certain users (e.g., engineers, field technician), preferably through implementing a role-based access mechanism. | relationship--5ae1cf3a-2603-4bf9-ace3-5b1ee5d8d757 | 21 September 2020 | 06 May 2022
M0800 | Authorization Enforcement | course-of-action--e0d38502-decb-481d-ad8b-b8f0a0c330bd | mitigation | mitigates | T0886 | Remote Services | attack-pattern--e1f9cdd2-9511-4fca-90d7-f3e92cfdd0bf | technique | Provide privileges corresponding to the restriction of a GUI session to control system operations (examples include HMI read-only vs. read-write modes). Ensure local users, such as operators and engineers, are giving prioritization over remote sessions and have the authority to regain control over a remote session if needed. Prevent remote access sessions (e.g., RDP, VNC) from taking over local sessions, especially those used for ICS control, especially HMIs. | relationship--4966e63c-ca05-466d-91f9-41d799a54471 | 12 April 2021 | 06 May 2022
M0946 | Boot Integrity | course-of-action--8ac1d6e1-b07f-476a-9732-84984ebc2405 | mitigation | mitigates | T0839 | Module Firmware | attack-pattern--efbf7888-f61b-4572-9c80-7e2965c60707 | technique | Check the integrity of the existing BIOS or EFI to determine if it is vulnerable to modification. Use Trusted Platform Module technology. (Citation: N/A) Move system's root of trust to hardware to prevent tampering with the SPI flash memory. (Citation: ESET Research Whitepapers September 2018) Technologies such as Intel Boot Guard can assist with this. (Citation: Intel) | relationship--0c284ce0-0be2-4164-b686-7c383b246aec | 21 September 2020 | 21 March 2023
M0946 | Boot Integrity | course-of-action--8ac1d6e1-b07f-476a-9732-84984ebc2405 | mitigation | mitigates | T0857 | System Firmware | attack-pattern--b9160e77-ea9e-4ba9-b1c8-53a3c466b13d | technique | Check the integrity of the existing BIOS or EFI to determine if it is vulnerable to modification. Use Trusted Platform Module technology. (Citation: N/A) Move system's root of trust to hardware to prevent tampering with the SPI flash memory. (Citation: ESET Research Whitepapers September 2018) Technologies such as Intel Boot Guard can assist with this. (Citation: Intel) | relationship--a47cd7b9-2b73-480c-a8ab-2dfa908e02ea | 21 September 2020 | 21 March 2023
M0945 | Code Signing | course-of-action--71eb7dad-07eb-4bbc-9df0-ac57bf2fba4a | mitigation | mitigates | T0849 | Masquerading | attack-pattern--ba203963-3182-41ac-af14-7e7ebc83cd61 | technique | Require signed binaries. | relationship--b9e82422-b072-494f-99c1-fcab07b90133 | 21 September 2020 | 06 May 2022
M0945 | Code Signing | course-of-action--71eb7dad-07eb-4bbc-9df0-ac57bf2fba4a | mitigation | mitigates | T0821 | Modify Controller Tasking | attack-pattern--09a61657-46e1-439e-b3ed-3e4556a78243 | technique | Utilize code signatures to verify the integrity and authenticity of programs installed on safety or control assets, including the associated controller tasking. | relationship--973f5884-a076-413e-ac96-f0bd01375fb6 | 13 April 2021 | 25 September 2023
M0945 | Code Signing | course-of-action--71eb7dad-07eb-4bbc-9df0-ac57bf2fba4a | mitigation | mitigates | T0889 | Modify Program | attack-pattern--fc5fda7e-6b2c-4457-b036-759896a2efa2 | technique | Utilize code signatures to verify the integrity and authenticity of programs installed on safety or control assets. | relationship--a91002fe-21b2-4417-9c23-af712a7a035c | 13 April 2021 | 25 September 2023
M0945 | Code Signing | course-of-action--71eb7dad-07eb-4bbc-9df0-ac57bf2fba4a | mitigation | mitigates | T0839 | Module Firmware | attack-pattern--efbf7888-f61b-4572-9c80-7e2965c60707 | technique | Devices should verify that firmware has been properly signed by the vendor before allowing installation. | relationship--46332a77-2fd6-4033-96cf-6163172775ec | 21 September 2020 | 06 May 2022
M0945 | Code Signing | course-of-action--71eb7dad-07eb-4bbc-9df0-ac57bf2fba4a | mitigation | mitigates | T0843 | Program Download | attack-pattern--be69c571-d746-4b1f-bdd0-c0c9817e9068 | technique | Utilize code signatures to verify the integrity and authenticity of programs downloaded to the device. | relationship--cb30d507-edc6-4197-947c-7b3a6e395c0d | 21 September 2020 | 25 September 2023
M0945 | Code Signing | course-of-action--71eb7dad-07eb-4bbc-9df0-ac57bf2fba4a | mitigation | mitigates | T0873 | Project File Infection | attack-pattern--e72425f8-9ae6-41d3-bfdb-e1b865e60722 | technique | Allow for code signing of any project files stored at rest to prevent unauthorized tampering. Ensure the signing keys are not easily accessible on the same system. | relationship--f9c29dd4-1c5e-4f7e-b60a-862319a6d0a0 | 21 September 2020 | 06 May 2022
M0945 | Code Signing | course-of-action--71eb7dad-07eb-4bbc-9df0-ac57bf2fba4a | mitigation | mitigates | T0851 | Rootkit | attack-pattern--3b6b9246-43f8-4c69-ad7a-2b11cfe0a0d9 | technique | Digital signatures may be used to ensure application DLLs are authentic prior to execution. | relationship--2971151c-0e8a-4567-84dc-01cf5dd35005 | 21 September 2020 | 06 May 2022
M0945 | Code Signing | course-of-action--71eb7dad-07eb-4bbc-9df0-ac57bf2fba4a | mitigation | mitigates | T0862 | Supply Chain Compromise | attack-pattern--5e0f75da-e108-4688-a6de-a4f07cc2cbe3 | technique | When available utilize hardware and software root-of-trust to verify the authenticity of a system. This may be achieved through cryptographic means, such as digital signatures or hashes, of critical software and firmware throughout the supply chain. | relationship--d6a2a1a8-8f5b-4e94-8fce-8edd8a17627a | 21 September 2020 | 06 May 2022
M0945 | Code Signing | course-of-action--71eb7dad-07eb-4bbc-9df0-ac57bf2fba4a | mitigation | mitigates | T0857 | System Firmware | attack-pattern--b9160e77-ea9e-4ba9-b1c8-53a3c466b13d | technique | Devices should verify that firmware has been properly signed by the vendor before allowing installation. | relationship--3be9d4d1-17e1-4f3e-b22a-edad8cf0c343 | 21 September 2020 | 06 May 2022
M0945 | Code Signing | course-of-action--71eb7dad-07eb-4bbc-9df0-ac57bf2fba4a | mitigation | mitigates | T0863 | User Execution | attack-pattern--2736b752-4ec5-4421-a230-8977dea7649c | technique | Prevent the use of unsigned executables, such as installers and scripts. | relationship--e09e253c-fd28-49ae-988e-1f80d769e8b8 | 21 September 2020 | 06 May 2022
M0802 | Communication Authenticity | course-of-action--c7257b6e-4159-4771-b1f3-2bb93adaecac | mitigation | mitigates | T0800 | Activate Firmware Update Mode | attack-pattern--19a71d1e-6334-4233-8260-b749cae37953 | technique | Protocols used for device management should authenticate all network messages to prevent unauthorized system changes. | relationship--afd63145-6033-49e4-ad43-d0b35fa5ed88 | 21 September 2020 | 06 May 2022
M0802 | Communication Authenticity | course-of-action--c7257b6e-4159-4771-b1f3-2bb93adaecac | mitigation | mitigates | T0830 | Adversary-in-the-Middle | attack-pattern--9a505987-ab05-4f46-a9a6-6441442eec3b | technique | Communication authenticity will ensure that any messages tampered with through AiTM can be detected, but cannot prevent eavesdropping on these. In addition, providing communication authenticity around various discovery protocols, such as DNS, can be used to prevent various AiTM procedures. | relationship--f6ff74c2-d088-4252-a8e0-189574863765 | 21 September 2020 | 21 March 2023
M0802 | Communication Authenticity | course-of-action--c7257b6e-4159-4771-b1f3-2bb93adaecac | mitigation | mitigates | T0858 | Change Operating Mode | attack-pattern--2883c520-7957-46ca-89bd-dab1ad53b601 | technique | Protocols used for device management should authenticate all network messages to prevent unauthorized system changes. | relationship--12a6c5bc-c685-4249-b8c6-e6d49aa2b9ed | 21 September 2020 | 06 May 2022
M0802 | Communication Authenticity | course-of-action--c7257b6e-4159-4771-b1f3-2bb93adaecac | mitigation | mitigates | T0868 | Detect Operating Mode | attack-pattern--2aa406ed-81c3-4c1d-ba83-cfbee5a2847a | technique | Protocols used for control functions should provide authenticity through MAC functions or digital signatures. If not, utilize bump-in-the-wire devices or VPNs to enforce communication authenticity between devices that are not capable of supporting this (e.g., legacy controllers, RTUs). | relationship--808c57e7-72ef-4860-b9ea-8ea072e2385a | 21 September 2020 | 06 May 2022
M0802 | Communication Authenticity | course-of-action--c7257b6e-4159-4771-b1f3-2bb93adaecac | mitigation | mitigates | T0816 | Device Restart/Shutdown | attack-pattern--25dfc8ad-bd73-4dfd-84a9-3c3d383f76e9 | technique | Protocols used for control functions should provide authenticity through MAC functions or digital signatures. If not, utilize bump-in-the-wire devices or VPNs to enforce communication authenticity between devices that are not capable of supporting this (e.g., legacy controllers, RTUs). | relationship--491455dc-f7c8-4e12-811b-b8c5c041b4c3 | 21 September 2020 | 06 May 2022
M0802 | Communication Authenticity | course-of-action--c7257b6e-4159-4771-b1f3-2bb93adaecac | mitigation | mitigates | T0831 | Manipulation of Control | attack-pattern--1af9e3fd-2bcc-414d-adbd-fe3b95c02ca1 | technique | Protocols used for control functions should provide authenticity through MAC functions or digital signatures. If not, utilize bump-in-the-wire devices or VPNs to enforce communication authenticity between devices that are not capable of supporting this (e.g., legacy controllers, RTUs). | relationship--b628d878-4f35-4580-8d42-26984d13821e | 21 September 2020 | 06 May 2022
M0802 | Communication Authenticity | course-of-action--c7257b6e-4159-4771-b1f3-2bb93adaecac | mitigation | mitigates | T0832 | Manipulation of View | attack-pattern--4c2e1408-9d68-4187-8e6b-a77bc52700ec | technique | Protocols used for control functions should provide authenticity through MAC functions or digital signatures. If not, utilize bump-in-the-wire devices or VPNs to enforce communication authenticity between devices that are not capable of supporting this (e.g., legacy controllers, RTUs). | relationship--41adaf0b-b7ae-4bdb-9a5b-567fd0911d7a | 21 September 2020 | 06 May 2022
M0802 | Communication Authenticity | course-of-action--c7257b6e-4159-4771-b1f3-2bb93adaecac | mitigation | mitigates | T0839 | Module Firmware | attack-pattern--efbf7888-f61b-4572-9c80-7e2965c60707 | technique | Protocols used for device management should authenticate all network messages to prevent unauthorized system changes. | relationship--7aa93b40-80da-4bb6-8a7c-88e5f5e44669 | 21 September 2020 | 06 May 2022
M0802 | Communication Authenticity | course-of-action--c7257b6e-4159-4771-b1f3-2bb93adaecac | mitigation | mitigates | T0861 | Point & Tag Identification | attack-pattern--25852363-5968-4673-b81d-341d5ed90bd1 | technique | Protocols used for control functions should provide authenticity through MAC functions or digital signatures. If not, utilize bump-in-the-wire devices or VPNs to enforce communication authenticity between devices that are not capable of supporting this (e.g., legacy controllers, RTUs). | relationship--dbdd9a97-81df-40b8-b72d-ac67d121b8b3 | 21 September 2020 | 06 May 2022
M0802 | Communication Authenticity | course-of-action--c7257b6e-4159-4771-b1f3-2bb93adaecac | mitigation | mitigates | T0843 | Program Download | attack-pattern--be69c571-d746-4b1f-bdd0-c0c9817e9068 | technique | Protocols used for device management should authenticate all network messages to prevent unauthorized system changes. | relationship--ebc34374-2dee-4dc1-b0b7-f31ae94dab11 | 21 September 2020 | 06 May 2022
M0802 | Communication Authenticity | course-of-action--c7257b6e-4159-4771-b1f3-2bb93adaecac | mitigation | mitigates | T0845 | Program Upload | attack-pattern--3067b85e-271e-4bc5-81ad-ab1a81d411e3 | technique | Protocols used for device management should authenticate all network messages to prevent unauthorized system changes. | relationship--0df0cb6d-0067-48b2-a33e-495415713ab7 | 21 September 2020 | 06 May 2022
M0802 | Communication Authenticity | course-of-action--c7257b6e-4159-4771-b1f3-2bb93adaecac | mitigation | mitigates | T0848 | Rogue Master | attack-pattern--b14395bd-5419-4ef4-9bd8-696936f509bb | technique | Protocols used for control functions should provide authenticity through MAC functions or digital signatures. If not, utilize bump-in-the-wire devices or VPNs to enforce communication authenticity between devices that are not capable of supporting this (e.g., legacy controllers, RTUs). | relationship--7db9687b-7099-4cb6-a040-bc32fc549a81 | 21 September 2020 | 06 May 2022
M0802 | Communication Authenticity | course-of-action--c7257b6e-4159-4771-b1f3-2bb93adaecac | mitigation | mitigates | T0856 | Spoof Reporting Message | attack-pattern--8535b71e-3c12-4258-a4ab-40257a1becc4 | technique | Protocols used for control functions should provide authenticity through MAC functions or digital signatures. If not, utilize bump-in-the-wire devices or VPNs to enforce communication authenticity between devices that are not capable of supporting this (e.g., legacy controllers, RTUs). | relationship--147c2158-b2af-4d88-9d59-594c67a9200e | 21 September 2020 | 06 May 2022
M0802 | Communication Authenticity | course-of-action--c7257b6e-4159-4771-b1f3-2bb93adaecac | mitigation | mitigates | T0857 | System Firmware | attack-pattern--b9160e77-ea9e-4ba9-b1c8-53a3c466b13d | technique | Protocols used for device management should authenticate all network messages to prevent unauthorized system changes. | relationship--234da455-b795-4788-bc5d-22b4b58b2dc7 | 21 September 2020 | 06 May 2022
M0802 | Communication Authenticity | course-of-action--c7257b6e-4159-4771-b1f3-2bb93adaecac | mitigation | mitigates | T0855 | Unauthorized Command Message | attack-pattern--40b300ba-f553-48bf-862e-9471b220d455 | technique | Protocols used for control functions should provide authenticity through MAC functions or digital signatures. If not, utilize bump-in-the-wire devices or VPNs to enforce communication authenticity between devices that are not capable of supporting this (e.g., legacy controllers, RTUs). | relationship--6e3c2c04-0838-4863-80a7-d73ef5ac6a64 | 21 September 2020 | 06 May 2022
M0802 | Communication Authenticity | course-of-action--c7257b6e-4159-4771-b1f3-2bb93adaecac | mitigation | mitigates | T0860 | Wireless Compromise | attack-pattern--2877063e-1851-48d2-bcc6-bc1d2733157e | technique | Do not inherently rely on the authenticity provided by the network/link layer (e.g., 802.11, LTE, 802.15.4), as link layer equipment may have long lifespans and protocol vulnerabilities may not be easily patched. Provide defense-in-depth by implementing authenticity within the associated application-layer protocol, or through a network-layer VPN. (Citation: CISA March 2010) Furthermore, ensure communication schemes provide strong replay protection, employing techniques such as timestamps or cryptographic nonces. | relationship--3ab912a4-70aa-45f8-b2ef-57113dde2cfa | 21 September 2020 | 06 May 2022
M0953 | Data Backup | course-of-action--ad12819e-3211-4291-b360-069f280cff0a | mitigation | mitigates | T0892 | Change Credential | attack-pattern--fab8fc7d-f27f-4fbb-9de6-44740aade05f | technique | Take and store data backups from end user systems and critical servers. Ensure backup and storage systems are hardened and kept separate from the corporate network to prevent compromise. Maintain and exercise incident response plans (Citation: Department of Homeland Security October 2009), including the management of gold-copy back-up images and configurations for key systems to enable quick recovery and response from adversarial activities that impact control, view, or availability. | relationship--a717ccc7-0fe6-4a83-951f-5a89037ed927 | 30 March 2023 | 30 March 2023
M0953 | Data Backup | course-of-action--ad12819e-3211-4291-b360-069f280cff0a | mitigation | mitigates | T0809 | Data Destruction | attack-pattern--493832d9-cea6-4b63-abe7-9a65a6473675 | technique | Utilize central storage servers for critical operations where possible (e.g., historians) and keep remote backups. For outstations, use local redundant storage for event recorders. Have backup control system platforms, preferably as hot-standbys to respond immediately to data destruction events. (Citation: National Institute of Standards and Technology April 2013) | relationship--6be4cef2-3d54-4cd8-97df-8a8b37c03605 | 21 September 2020 | 06 May 2022
M0953 | Data Backup | course-of-action--ad12819e-3211-4291-b360-069f280cff0a | mitigation | mitigates | T0813 | Denial of Control | attack-pattern--e33c7ecc-5a38-497f-beb2-a9a2049a4c20 | technique | Take and store data backups from end user systems and critical servers. Ensure backup and storage systems are hardened and kept separate from the corporate network to prevent compromise. Maintain and exercise incident response plans (Citation: Department of Homeland Security October 2009), including the management of gold-copy back-up images and configurations for key systems to enable quick recovery and response from adversarial activities that impact control, view, or availability. | relationship--44c857cf-7a4e-405a-87ca-7f6d79000589 | 21 September 2020 | 19 October 2022
M0953 | Data Backup | course-of-action--ad12819e-3211-4291-b360-069f280cff0a | mitigation | mitigates | T0815 | Denial of View | attack-pattern--56ddc820-6cfb-407f-850b-52c035d123ac | technique | Take and store data backups from end user systems and critical servers. Ensure backup and storage systems are hardened and kept separate from the corporate network to prevent compromise. Maintain and exercise incident response plans (Citation: Department of Homeland Security October 2009), including the management of gold-copy back-up images and configurations for key systems to enable quick recovery and response from adversarial activities that impact control, view, or availability. | relationship--c2fe42b4-6750-4b51-86b7-6c37fbfdef2d | 21 September 2020 | 19 October 2022
M0953 | Data Backup | course-of-action--ad12819e-3211-4291-b360-069f280cff0a | mitigation | mitigates | T0826 | Loss of Availability | attack-pattern--b5b9bacb-97f2-4249-b804-47fd44de1f95 | technique | Take and store data backups from end user systems and critical servers. Ensure backup and storage systems are hardened and kept separate from the corporate network to prevent compromise. Maintain and exercise incident response plans (Citation: Department of Homeland Security October 2009), including the management of gold-copy back-up images and configurations for key systems to enable quick recovery and response from adversarial activities that impact control, view, or availability. | relationship--b8d6e550-18fe-49ad-9964-7802bbe0cb58 | 21 September 2020 | 19 October 2022
M0953 | Data Backup | course-of-action--ad12819e-3211-4291-b360-069f280cff0a | mitigation | mitigates | T0827 | Loss of Control | attack-pattern--a81696ef-c106-482c-8f80-59c30f2569fb | technique | Take and store data backups from end user systems and critical servers. Ensure backup and storage systems are hardened and kept separate from the corporate network to prevent compromise. Maintain and exercise incident response plans (Citation: Department of Homeland Security October 2009), including the management of gold-copy back-up images and configurations for key systems to enable quick recovery and response from adversarial activities that impact control, view, or availability. | relationship--6ad39b3a-a962-457f-852c-be7fc615e22f | 21 September 2020 | 19 October 2022
M0953 | Data Backup | course-of-action--ad12819e-3211-4291-b360-069f280cff0a | mitigation | mitigates | T0828 | Loss of Productivity and Revenue | attack-pattern--63b6942d-8359-4506-bfb3-cf87aa8120ee | technique | Take and store data backups from end user systems and critical servers. Ensure backup and storage systems are hardened and kept separate from the corporate network to prevent compromise. Maintain and exercise incident response plans (Citation: Department of Homeland Security October 2009), including the management of gold-copy back-up images and configurations for key systems to enable quick recovery and response from adversarial activities that impact control, view, or availability. | relationship--dda89758-9d0b-446d-b594-85acc7f9cb90 | 21 September 2020 | 19 October 2022
M0953 | Data Backup | course-of-action--ad12819e-3211-4291-b360-069f280cff0a | mitigation | mitigates | T0829 | Loss of View | attack-pattern--138979ba-0430-4de6-a128-2fc0b056ba36 | technique | Take and store data backups from end user systems and critical servers. Ensure backup and storage systems are hardened and kept separate from the corporate network to prevent compromise. Maintain and exercise incident response plans (Citation: Department of Homeland Security October 2009), including the management of gold-copy back-up images and configurations for key systems to enable quick recovery and response from adversarial activities that impact control, view, or availability. | relationship--eecca3e7-4db5-40d4-b04c-13f84701acb3 | 21 September 2020 | 19 October 2022
M0953 | Data Backup | course-of-action--ad12819e-3211-4291-b360-069f280cff0a | mitigation | mitigates | T0831 | Manipulation of Control | attack-pattern--1af9e3fd-2bcc-414d-adbd-fe3b95c02ca1 | technique | Take and store data backups from end user systems and critical servers. Ensure backup and storage systems are hardened and kept separate from the corporate network to prevent compromise. Maintain and exercise incident response plans (Citation: Department of Homeland Security October 2009), including the management of gold-copy back-up images and configurations for key systems to enable quick recovery and response from adversarial activities that impact control, view, or availability. | relationship--578117b2-0f4b-4d75-a2dc-3ee45976e616 | 21 September 2020 | 19 October 2022
M0953 | Data Backup | course-of-action--ad12819e-3211-4291-b360-069f280cff0a | mitigation | mitigates | T0832 | Manipulation of View | attack-pattern--4c2e1408-9d68-4187-8e6b-a77bc52700ec | technique | Take and store data backups from end user systems and critical servers. Ensure backup and storage systems are hardened and kept separate from the corporate network to prevent compromise. Maintain and exercise incident response plans (Citation: Department of Homeland Security October 2009), including the management of gold-copy back-up images and configurations for key systems to enable quick recovery and response from adversarial activities that impact control, view, or availability. | relationship--c64f2ed2-f7a7-4333-b0d3-d687ffb7ad6b | 21 September 2020 | 19 October 2022
M0803 | Data Loss Prevention | course-of-action--337c4e2a-21a7-4d9a-bfee-9efd6cebf0e5 | mitigation | mitigates | T0893 | Data from Local System | attack-pattern--fa3aa267-da22-4bdd-961f-03223322a8d5 | technique | Data loss prevention can restrict access to sensitive data and detect sensitive data that is unencrypted. | relationship--8f7ccb2b-de2a-4a5c-9f1e-d5e58e69efa8 | 30 March 2023 | 30 March 2023
M0803 | Data Loss Prevention | course-of-action--337c4e2a-21a7-4d9a-bfee-9efd6cebf0e5 | mitigation | mitigates | T0882 | Theft of Operational Information | attack-pattern--b7e13ee8-182c-4f19-92a4-a88d7d855d54 | technique | Apply DLP to protect the confidentiality of information related to operational processes, facility locations, device configurations, programs, or databases that may have information that can be used to infer organizational trade-secrets, recipes, and other intellectual property (IP). | relationship--bc74ff8f-d5fa-40fb-8c0b-f16af3ff36e3 | 21 September 2020 | 06 May 2022
M0942 | Disable or Remove Feature or Program | course-of-action--d0909119-2f71-4923-87db-b649881672d7 | mitigation | mitigates | T0830 | Adversary-in-the-Middle | attack-pattern--9a505987-ab05-4f46-a9a6-6441442eec3b | technique | Disable unnecessary legacy network protocols that may be used for AiTM if applicable. | relationship--d16e8909-d055-4174-aeb1-22c0613b2f73 | 21 September 2020 | 21 March 2023
M0942 | Disable or Remove Feature or Program | course-of-action--d0909119-2f71-4923-87db-b649881672d7 | mitigation | mitigates | T0807 | Command-Line Interface | attack-pattern--24a9253e-8948-4c98-b751-8e2aee53127c | technique | Consider removing or restricting features that are unnecessary to an asset's intended function within the control environment. | relationship--7c2edd6c-5189-4ba9-af3d-bdaff4a699ca | 21 September 2020 | 06 May 2022
M0942 | Disable or Remove Feature or Program | course-of-action--d0909119-2f71-4923-87db-b649881672d7 | mitigation | mitigates | T0885 | Commonly Used Port | attack-pattern--e6c31185-8040-4267-83d3-b217b8a92f07 | technique | Ensure that unnecessary ports and services are closed to prevent risk of discovery and potential exploitation. | relationship--ca64a927-f050-41b3-80d3-93d22cdef26a | 21 September 2020 | 06 May 2022
M0942 | Disable or Remove Feature or Program | course-of-action--d0909119-2f71-4923-87db-b649881672d7 | mitigation | mitigates | T0816 | Device Restart/Shutdown | attack-pattern--25dfc8ad-bd73-4dfd-84a9-3c3d383f76e9 | technique | Ensure remote commands that enable device shutdown are disabled if they are not necessary. Examples include DNP3's 0x0D function code or unnecessary device management functions. | relationship--8ca2fe75-9bb3-4af5-8fee-accd33d6d2ec | 21 September 2020 | 06 May 2022
M0942 | Disable or Remove Feature or Program | course-of-action--d0909119-2f71-4923-87db-b649881672d7 | mitigation | mitigates | T0866 | Exploitation of Remote Services | attack-pattern--85a45294-08f1-4539-bf00-7da08aa7b0ee | technique | Ensure that unnecessary ports and services are closed to prevent risk of discovery and potential exploitation. | relationship--4369da69-bb09-4cc8-8600-081a450f50e0 | 21 September 2020 | 06 May 2022
M0942 | Disable or Remove Feature or Program | course-of-action--d0909119-2f71-4923-87db-b649881672d7 | mitigation | mitigates | T0822 | External Remote Services | attack-pattern--8d2f3bab-507c-4424-b58b-edc977bd215c | technique | Consider removal of remote services which are not regularly in use, or only enabling them when required (e.g., vendor remote access). Ensure all external remote access point (e.g., jump boxes, VPN concentrator) are configured with least functionality, especially the removal of unnecessary services. (Citation: Department of Homeland Security September 2016) | relationship--a847aa03-ea56-47d1-8f4e-f9e0dd9707a0 | 21 September 2020 | 06 May 2022
M0942 | Disable or Remove Feature or Program | course-of-action--d0909119-2f71-4923-87db-b649881672d7 | mitigation | mitigates | T0847 | Replication Through Removable Media | attack-pattern--c267bbee-bb59-47fe-85e0-3ed210337c21 | technique | Consider the disabling of features such as AutoRun. | relationship--d8f45959-e0fc-4b4f-a074-a3acea926300 | 21 September 2020 | 06 May 2022
M0942 | Disable or Remove Feature or Program | course-of-action--d0909119-2f71-4923-87db-b649881672d7 | mitigation | mitigates | T0853 | Scripting | attack-pattern--2dc2b567-8821-49f9-9045-8740f3d0b958 | technique | Consider removal or disabling of programs and features which may be used to run malicious scripts (e.g., scripting language IDEs, PowerShell, visual studio). | relationship--590bdd67-31ef-4edd-b2ac-2bd1b98da19c | 21 September 2020 | 06 May 2022
M0808 | Encrypt Network Traffic | course-of-action--7f153c28-e5f1-4764-88fb-eea1d9b0ad4a | mitigation | mitigates | T0839 | Module Firmware | attack-pattern--efbf7888-f61b-4572-9c80-7e2965c60707 | technique | The encryption of firmware should be considered to prevent adversaries from identifying possible vulnerabilities within the firmware. | relationship--41b87fd8-6e4d-4e53-a282-c85292fdaa22 | 21 September 2020 | 06 May 2022
M0808 | Encrypt Network Traffic | course-of-action--7f153c28-e5f1-4764-88fb-eea1d9b0ad4a | mitigation | mitigates | T0842 | Network Sniffing | attack-pattern--38213338-1aab-479d-949b-c81b66ccca5c | technique | Ensure that wired and/or wireless traffic is encrypted when feasible. Use best practices for authentication protocols, such as Kerberos, and ensure web traffic that may contain credentials is protected by SSL/TLS. (Citation: Keith Stouffer May 2015) | relationship--c5fd0969-c151-4849-94c2-83e2e208cff7 | 21 September 2020 | 06 May 2022
M0808 | Encrypt Network Traffic | course-of-action--7f153c28-e5f1-4764-88fb-eea1d9b0ad4a | mitigation | mitigates | T0857 | System Firmware | attack-pattern--b9160e77-ea9e-4ba9-b1c8-53a3c466b13d | technique | The encryption of firmware should be considered to prevent adversaries from identifying possible vulnerabilities within the firmware. | relationship--43bdf580-b98f-49cf-92d5-3dac50450c86 | 21 September 2020 | 06 May 2022
M0808 | Encrypt Network Traffic | course-of-action--7f153c28-e5f1-4764-88fb-eea1d9b0ad4a | mitigation | mitigates | T0860 | Wireless Compromise | attack-pattern--2877063e-1851-48d2-bcc6-bc1d2733157e | technique | Utilize strong cryptographic techniques and protocols to prevent eavesdropping on network communications. | relationship--b363cbbb-679c-47e0-8ad0-af98ebf51e60 | 21 September 2020 | 06 May 2022
M0808 | Encrypt Network Traffic | course-of-action--7f153c28-e5f1-4764-88fb-eea1d9b0ad4a | mitigation | mitigates | T0887 | Wireless Sniffing | attack-pattern--0fe075d5-beac-4d02-b93e-0f874997db72 | technique | Utilize strong cryptographic techniques and protocols to prevent eavesdropping on network communications. (Citation: Bastille April 2017) | relationship--3478c49c-594b-4224-b7f9-2b0b09c67288 | 21 September 2020 | 06 May 2022
M0941 | Encrypt Sensitive Information | course-of-action--9f99fcfd-772e-4e63-9d39-e45612e546dc | mitigation | mitigates | T0811 | Data from Information Repositories | attack-pattern--3405891b-16aa-4bd7-bd7c-733501f9b20f | technique | Information which is sensitive to the operation and architecture of the process environment may be encrypted to ensure confidentiality and restrict access to only those who need to know. (Citation: Keith Stouffer May 2015) (Citation: National Institute of Standards and Technology April 2013) | relationship--50a2b289-7bce-405d-8515-c2b5424cce5c | 21 September 2020 | 06 May 2022
M0941 | Encrypt Sensitive Information | course-of-action--9f99fcfd-772e-4e63-9d39-e45612e546dc | mitigation | mitigates | T0893 | Data from Local System | attack-pattern--fa3aa267-da22-4bdd-961f-03223322a8d5 | technique | Information which is sensitive to the operation and architecture of the process environment may be encrypted to ensure confidentiality and restrict access to only those who need to know. (Citation: Keith Stouffer May 2015) (Citation: National Institute of Standards and Technology April 2013) | relationship--03e80e3c-28b9-4e7f-8b17-7c86d1483b91 | 30 March 2023 | 30 March 2023
M0941 | Encrypt Sensitive Information | course-of-action--9f99fcfd-772e-4e63-9d39-e45612e546dc | mitigation | mitigates | T0839 | Module Firmware | attack-pattern--efbf7888-f61b-4572-9c80-7e2965c60707 | technique | The encryption of firmware should be considered to prevent adversaries from identifying possible vulnerabilities within the firmware. | relationship--09977105-562f-4f45-a151-27a11a18031e | 21 September 2020 | 06 May 2022
M0941 | Encrypt Sensitive Information | course-of-action--9f99fcfd-772e-4e63-9d39-e45612e546dc | mitigation | mitigates | T0873 | Project File Infection | attack-pattern--e72425f8-9ae6-41d3-bfdb-e1b865e60722 | technique | When at rest, project files should be encrypted to prevent unauthorized changes. (Citation: National Institute of Standards and Technology April 2013) | relationship--c78f497f-01c3-4efb-aa74-92b700b9c02b | 21 September 2020 | 06 May 2022
M0941 | Encrypt Sensitive Information | course-of-action--9f99fcfd-772e-4e63-9d39-e45612e546dc | mitigation | mitigates | T0857 | System Firmware | attack-pattern--b9160e77-ea9e-4ba9-b1c8-53a3c466b13d | technique | The encryption of firmware should be considered to prevent adversaries from identifying possible vulnerabilities within the firmware. | relationship--cf8ac499-8c1c-4615-b933-7587f1b9488b | 21 September 2020 | 06 May 2022
M0941 | Encrypt Sensitive Information | course-of-action--9f99fcfd-772e-4e63-9d39-e45612e546dc | mitigation | mitigates | T0882 | Theft of Operational Information | attack-pattern--b7e13ee8-182c-4f19-92a4-a88d7d855d54 | technique | Encrypt any operational data with strong confidentiality requirements, including organizational trade-secrets, recipes, and other intellectual property (IP). | relationship--cb4d802e-df5b-4017-81dd-47f65fff23a3 | 21 September 2020 | 06 May 2022
M0941 | Encrypt Sensitive Information | course-of-action--9f99fcfd-772e-4e63-9d39-e45612e546dc | mitigation | mitigates | T0864 | Transient Cyber Asset | attack-pattern--35392fb4-a31d-4c6a-b9f2-1c65b7f5e6b9 | technique | Consider implementing full disk encryption, especially if engineering workstations are transient assets that are more likely to be lost, stolen, or tampered with. (Citation: National Institute of Standards and Technology April 2013) | relationship--2fbb7867-79c5-4d45-9876-98c4041dd72e | 14 October 2021 | 06 May 2022
M0938 | Execution Prevention | course-of-action--4fa717d9-cabe-47c8-8cdd-86e9e2e37f30 | mitigation | mitigates | T0807 | Command-Line Interface | attack-pattern--24a9253e-8948-4c98-b751-8e2aee53127c | technique | Execution prevention may block malicious software from accessing protected resources through the command line interface. | relationship--75366cbf-e45f-4cfd-9e76-5af4dfe10766 | 21 September 2020 | 06 May 2022
M0938 | Execution Prevention | course-of-action--4fa717d9-cabe-47c8-8cdd-86e9e2e37f30 | mitigation | mitigates | T0871 | Execution through API | attack-pattern--5a2610f6-9fff-41e1-bc27-575ca20383d4 | technique | Minimize the exposure of API calls that allow the execution of code. | relationship--3d676c1b-2650-4599-8a57-790c55f9977d | 21 September 2020 | 06 May 2022
M0938 | Execution Prevention | course-of-action--4fa717d9-cabe-47c8-8cdd-86e9e2e37f30 | mitigation | mitigates | T0849 | Masquerading | attack-pattern--ba203963-3182-41ac-af14-7e7ebc83cd61 | technique | Use tools that restrict program execution via application control by attributes other than file name for common system and application utilities. | relationship--cca191a1-3c50-4d4f-8f79-4247e58af610 | 21 September 2020 | 06 May 2022
M0938 | Execution Prevention | course-of-action--4fa717d9-cabe-47c8-8cdd-86e9e2e37f30 | mitigation | mitigates | T0834 | Native API | attack-pattern--b52870cc-83f3-473c-b895-72d91751030b | technique | Minimize the exposure of API calls that allow the execution of code. | relationship--446c95ea-5178-4ae9-8f92-cb20dd50f7de | 13 April 2021 | 06 May 2022
M0938 | Execution Prevention | course-of-action--4fa717d9-cabe-47c8-8cdd-86e9e2e37f30 | mitigation | mitigates | T0853 | Scripting | attack-pattern--2dc2b567-8821-49f9-9045-8740f3d0b958 | technique | Execution prevention may prevent malicious scripts from accessing protected resources. | relationship--2f64b5aa-7e4d-4a5e-9960-69a63ad25083 | 21 September 2020 | 06 May 2022
M0938 | Execution Prevention | course-of-action--4fa717d9-cabe-47c8-8cdd-86e9e2e37f30 | mitigation | mitigates | T0894 | System Binary Proxy Execution | attack-pattern--1c5cf58c-a34a-40d7-82f4-f987cdfc2b91 | technique | Disallow the execution of applications/programs which are not required for normal system functions, including any specific command-line arguments which may allow the execution of proxy commands or application binaries. | relationship--337f366d-3d76-470c-8ee2-0e2252648282 | 25 March 2024 | 25 March 2024
M0938 | Execution Prevention | course-of-action--4fa717d9-cabe-47c8-8cdd-86e9e2e37f30 | mitigation | mitigates | T0863 | User Execution | attack-pattern--2736b752-4ec5-4421-a230-8977dea7649c | technique | Application control may be able to prevent the running of executables masquerading as other files. | relationship--07f4d65d-4572-450f-8cb2-908fee97bd67 | 21 September 2020 | 06 May 2022
M0950 | Exploit Protection | course-of-action--49363b74-d506-4342-bd63-320586ebadb9 | mitigation | mitigates | T0817 | Drive-by Compromise | attack-pattern--7830cfcf-b268-4ac0-a69e-73c6affbae9a | technique | Utilize exploit protection to prevent activities which may be exploited through malicious web sites. | relationship--e5afc447-a241-4773-9a8a-3d6fd205d926 | 21 September 2020 | 06 May 2022
M0950 | Exploit Protection | course-of-action--49363b74-d506-4342-bd63-320586ebadb9 | mitigation | mitigates | T0819 | Exploit Public-Facing Application | attack-pattern--32632a95-6856-47b9-9ab7-fea5cd7dce00 | technique | Web Application Firewalls may be used to limit exposure of applications to prevent exploit traffic from reaching the application. (Citation: Karen Scarfone; Paul Hoffman September 2009) | relationship--ad7fd147-066e-4ed5-aa9d-7b2f1771150d | 21 September 2020 | 06 May 2022
M0950 | Exploit Protection | course-of-action--49363b74-d506-4342-bd63-320586ebadb9 | mitigation | mitigates | T0820 | Exploitation for Evasion | attack-pattern--9f947a1c-3860-48a8-8af0-a2dfa3efde03 | technique | Security applications that look for behavior used during exploitation such as Windows Defender Exploit Guard (WDEG) and the Enhanced Mitigation Experience Toolkit (EMET) can be used to mitigate some exploitation behavior. (Citation: Microsoft Security Response Center August 2017) Control flow integrity checking is another way to potentially identify and stop a software exploit from occurring. (Citation: Wikipedia) Many of these protections depend on the architecture and target application binary for compatibility and may not work for all software or services targeted. | relationship--238f967a-0c29-4aa3-bbb5-3dc593473bbf | 21 September 2020 | 21 March 2023
M0950 | Exploit Protection | course-of-action--49363b74-d506-4342-bd63-320586ebadb9 | mitigation | mitigates | T0890 | Exploitation for Privilege Escalation | attack-pattern--cfe68e93-ce94-4c0f-a57d-3aa72cedd618 | technique | Security applications that look for behavior used during exploitation such as Windows Defender Exploit Guard (WDEG) and the Enhanced Mitigation Experience Toolkit (EMET) can be used to mitigate some exploitation behavior. (Citation: Microsoft Security Response Center August 2017) Control flow integrity checking is another way to potentially identify and stop a software exploit from occurring. (Citation: Wikipedia) Many of these protections depend on the architecture and target application binary for compatibility and may not work for all software or services targeted. | relationship--3b6567a9-6213-4db4-a069-1a86b1098b63 | 13 April 2021 | 21 March 2023
M0950 | Exploit Protection | course-of-action--49363b74-d506-4342-bd63-320586ebadb9 | mitigation | mitigates | T0866 | Exploitation of Remote Services | attack-pattern--85a45294-08f1-4539-bf00-7da08aa7b0ee | technique | Security applications that look for behavior used during exploitation such as Windows Defender Exploit Guard (WDEG) and the Enhanced Mitigation Experience Toolkit (EMET) can be used to mitigate some exploitation behavior. (Citation: Microsoft Security Response Center August 2017) Control flow integrity checking is another way to potentially identify and stop a software exploit from occurring. (Citation: Wikipedia) Many of these protections depend on the architecture and target application binary for compatibility and may not work for all software or services targeted. | relationship--47f15a06-8675-4698-833d-bd141ed9e755 | 21 September 2020 | 21 March 2023
M0937 | Filter Network Traffic | course-of-action--11f242bc-3121-438c-84b2-5cbd46a4bb17 | mitigation | mitigates | T0800 | Activate Firmware Update Mode | attack-pattern--19a71d1e-6334-4233-8260-b749cae37953 | technique | Filter for protocols and payloads associated with firmware activation or updating activity. | relationship--ee89466e-0655-4217-844d-fb8ea4f76247 | 21 September 2020 | 06 May 2022
M0937 | Filter Network Traffic | course-of-action--11f242bc-3121-438c-84b2-5cbd46a4bb17 | mitigation | mitigates | T0806 | Brute Force I/O | attack-pattern--8e7089d3-fba2-44f8-94a8-9a79c53920c4 | technique | Allow/denylists can be used to block access when excessive I/O connections are detected from a system or device during a specified time period. | relationship--9a44b2a8-9f4c-43df-9174-1cba6e165886 | 21 September 2020 | 06 May 2022
M0937 | Filter Network Traffic | course-of-action--11f242bc-3121-438c-84b2-5cbd46a4bb17 | mitigation | mitigates | T0884 | Connection Proxy | attack-pattern--d67adac8-e3b9-44f9-9e6d-6c2a7d69dbe4 | technique | Traffic to known anonymity networks and C2 infrastructure can be blocked through the use of network allow and block lists. It should be noted that this kind of blocking may be circumvented by other techniques likeDomain Fronting. | relationship--7bfaf0ff-6d88-460f-aa32-3fb0267b4f20 | 21 September 2020 | 06 May 2022
M0937 | Filter Network Traffic | course-of-action--11f242bc-3121-438c-84b2-5cbd46a4bb17 | mitigation | mitigates | T0868 | Detect Operating Mode | attack-pattern--2aa406ed-81c3-4c1d-ba83-cfbee5a2847a | technique | Perform inline allowlisting of automation protocol commands to prevent devices from sending unauthorized command or reporting messages. Allow/denylist techniques need to be designed with sufficient accuracy to prevent the unintended blocking of valid messages. | relationship--64db6a39-64d2-4999-97d7-91c28c32f42e | 21 September 2020 | 06 May 2022
M0937 | Filter Network Traffic | course-of-action--11f242bc-3121-438c-84b2-5cbd46a4bb17 | mitigation | mitigates | T0816 | Device Restart/Shutdown | attack-pattern--25dfc8ad-bd73-4dfd-84a9-3c3d383f76e9 | technique | Application denylists can be used to block automation protocol functions used to initiate device shutdowns or restarts, such as DNP3's 0x0D function code, or vulnerabilities that can be used to trigger device shutdowns (e.g., CVE-2014-9195, CVE-2015-5374). | relationship--ca768c2a-0f14-471c-90a5-bce649e88d51 | 21 September 2020 | 06 May 2022
M0937 | Filter Network Traffic | course-of-action--11f242bc-3121-438c-84b2-5cbd46a4bb17 | mitigation | mitigates | T0839 | Module Firmware | attack-pattern--efbf7888-f61b-4572-9c80-7e2965c60707 | technique | Filter for protocols and payloads associated with firmware activation or updating activity. | relationship--3da977ab-c863-4e6f-a5b7-68173160da00 | 21 September 2020 | 06 May 2022
M0937 | Filter Network Traffic | course-of-action--11f242bc-3121-438c-84b2-5cbd46a4bb17 | mitigation | mitigates | T0861 | Point & Tag Identification | attack-pattern--25852363-5968-4673-b81d-341d5ed90bd1 | technique | Perform inline allowlisting of automation protocol commands to prevent devices from sending unauthorized command or reporting messages. Allow/denylist techniques need to be designed with sufficient accuracy to prevent the unintended blocking of valid messages. | relationship--686cbd74-ef49-4e77-9599-21777d3a4738 | 21 September 2020 | 06 May 2022
M0937 | Filter Network Traffic | course-of-action--11f242bc-3121-438c-84b2-5cbd46a4bb17 | mitigation | mitigates | T0843 | Program Download | attack-pattern--be69c571-d746-4b1f-bdd0-c0c9817e9068 | technique | Filter for protocols and payloads associated with program download activity to prevent unauthorized device configurations. | relationship--366a4cd1-aa95-4985-9d80-b45a2551e298 | 21 September 2020 | 06 May 2022
M0937 | Filter Network Traffic | course-of-action--11f242bc-3121-438c-84b2-5cbd46a4bb17 | mitigation | mitigates | T0845 | Program Upload | attack-pattern--3067b85e-271e-4bc5-81ad-ab1a81d411e3 | technique | Filter for protocols and payloads associated with program upload activity to prevent unauthorized access to device configurations. | relationship--baf4bd30-4213-43c3-b70c-54418e734caf | 21 September 2020 | 06 May 2022
M0937 | Filter Network Traffic | course-of-action--11f242bc-3121-438c-84b2-5cbd46a4bb17 | mitigation | mitigates | T0886 | Remote Services | attack-pattern--e1f9cdd2-9511-4fca-90d7-f3e92cfdd0bf | technique | Filter application-layer protocol messages for remote services to block any unauthorized activity. | relationship--f0c8a954-c1a0-453a-9c1d-484305abdab2 | 12 April 2021 | 06 May 2022
M0937 | Filter Network Traffic | course-of-action--11f242bc-3121-438c-84b2-5cbd46a4bb17 | mitigation | mitigates | T0848 | Rogue Master | attack-pattern--b14395bd-5419-4ef4-9bd8-696936f509bb | technique | Perform inline allowlisting of automation protocol commands to prevent devices from sending unauthorized command or reporting messages. Allow/denylist techniques need to be designed with sufficient accuracy to prevent the unintended blocking of valid reporting messages. | relationship--575f0e0b-d68d-432b-abb3-cbd3e641fc88 | 21 September 2020 | 06 May 2022
M0937 | Filter Network Traffic | course-of-action--11f242bc-3121-438c-84b2-5cbd46a4bb17 | mitigation | mitigates | T0856 | Spoof Reporting Message | attack-pattern--8535b71e-3c12-4258-a4ab-40257a1becc4 | technique | Perform inline allowlisting of automation protocol commands to prevent devices from sending unauthorized command or reporting messages. Allow/denylist techniques need to be designed with sufficient accuracy to prevent the unintended blocking of valid reporting messages. | relationship--d08fdedd-12f6-4681-9167-70d070432dee | 21 September 2020 | 06 May 2022
M0937 | Filter Network Traffic | course-of-action--11f242bc-3121-438c-84b2-5cbd46a4bb17 | mitigation | mitigates | T0857 | System Firmware | attack-pattern--b9160e77-ea9e-4ba9-b1c8-53a3c466b13d | technique | Filter for protocols and payloads associated with firmware activation or updating activity. | relationship--dc46ffc2-eac7-4491-8d2a-46cf8e2e963f | 21 September 2020 | 06 May 2022
M0937 | Filter Network Traffic | course-of-action--11f242bc-3121-438c-84b2-5cbd46a4bb17 | mitigation | mitigates | T0855 | Unauthorized Command Message | attack-pattern--40b300ba-f553-48bf-862e-9471b220d455 | technique | Perform inline allowlisting of automation protocol commands to prevent devices from sending unauthorized command or reporting messages. Allow/denylist techniques need to be designed with sufficient accuracy to prevent the unintended blocking of valid messages. | relationship--48489baf-56c2-423e-964a-0a61688e4a19 | 21 September 2020 | 06 May 2022
M0937 | Filter Network Traffic | course-of-action--11f242bc-3121-438c-84b2-5cbd46a4bb17 | mitigation | mitigates | T0859 | Valid Accounts | attack-pattern--cd2c76a4-5e23-4ca5-9c40-d5e0604f7101 | technique | Consider using IP allowlisting along with user account management to ensure that data access is restricted not only to valid users but only from expected IP ranges to mitigate the use of stolen credentials to access data. | relationship--5dfa5bad-8b0b-4884-bf01-04ea89e3ccf7 | 21 September 2020 | 06 May 2022
M0804 | Human User Authentication | course-of-action--66cfe23e-34b6-4583-b178-ed6a412db2b0 | mitigation | mitigates | T0800 | Activate Firmware Update Mode | attack-pattern--19a71d1e-6334-4233-8260-b749cae37953 | technique | Devices that allow remote management of firmware should require authentication before allowing any changes. The authentication mechanisms should also support [Account Use Policies](https://attack.mitre.org/mitigations/M0936), [Password Policies](https://attack.mitre.org/mitigations/M0927), and [User Account Management](https://attack.mitre.org/mitigations/M0918) | relationship--63453d2f-30f6-40ab-b32c-506d940ecd20 | 21 September 2020 | 08 March 2023
M0804 | Human User Authentication | course-of-action--66cfe23e-34b6-4583-b178-ed6a412db2b0 | mitigation | mitigates | T0858 | Change Operating Mode | attack-pattern--2883c520-7957-46ca-89bd-dab1ad53b601 | technique | All field controllers should require users to authenticate for all remote or local management sessions. The authentication mechanisms should also support [Account Use Policies](https://attack.mitre.org/mitigations/M0936), [Password Policies](https://attack.mitre.org/mitigations/M0927), and [User Account Management](https://attack.mitre.org/mitigations/M0918). | relationship--22448288-32d9-4d2c-be16-0784e119fff1 | 21 September 2020 | 08 March 2023
M0804 | Human User Authentication | course-of-action--66cfe23e-34b6-4583-b178-ed6a412db2b0 | mitigation | mitigates | T0885 | Commonly Used Port | attack-pattern--e6c31185-8040-4267-83d3-b217b8a92f07 | technique | All field controllers should require users to authenticate for all remote or local management sessions. The authentication mechanisms should also support [Account Use Policies](https://attack.mitre.org/mitigations/M0936), [Password Policies](https://attack.mitre.org/mitigations/M0927), and [User Account Management](https://attack.mitre.org/mitigations/M0918). | relationship--0a5d2136-e1f5-4a54-be64-a558f918bf0d | 21 September 2020 | 08 March 2023
M0804 | Human User Authentication | course-of-action--66cfe23e-34b6-4583-b178-ed6a412db2b0 | mitigation | mitigates | T0868 | Detect Operating Mode | attack-pattern--2aa406ed-81c3-4c1d-ba83-cfbee5a2847a | technique | All field controllers should require users to authenticate for all remote or local management sessions. The authentication mechanisms should also support [Account Use Policies](https://attack.mitre.org/mitigations/M0936), [Password Policies](https://attack.mitre.org/mitigations/M0927), and [User Account Management](https://attack.mitre.org/mitigations/M0918). | relationship--49d38b21-5ce5-48d9-a356-639fc6c7a53d | 21 September 2020 | 08 March 2023
M0804 | Human User Authentication | course-of-action--66cfe23e-34b6-4583-b178-ed6a412db2b0 | mitigation | mitigates | T0816 | Device Restart/Shutdown | attack-pattern--25dfc8ad-bd73-4dfd-84a9-3c3d383f76e9 | technique | All field controllers should require users to authenticate for all remote or local management sessions. The authentication mechanisms should also support [Account Use Policies](https://attack.mitre.org/mitigations/M0936), [Password Policies](https://attack.mitre.org/mitigations/M0927), and [User Account Management](https://attack.mitre.org/mitigations/M0918). | relationship--3a6cd53d-0d4e-4cf8-8edf-f9ebde4faac4 | 21 September 2020 | 08 March 2023
M0804 | Human User Authentication | course-of-action--66cfe23e-34b6-4583-b178-ed6a412db2b0 | mitigation | mitigates | T0871 | Execution through API | attack-pattern--5a2610f6-9fff-41e1-bc27-575ca20383d4 | technique | All APIs on remote systems or local processes should require the authentication of users before executing any code or system changes. | relationship--dded2d68-35c7-42c4-af10-efe7731673e3 | 21 September 2020 | 06 May 2022
M0804 | Human User Authentication | course-of-action--66cfe23e-34b6-4583-b178-ed6a412db2b0 | mitigation | mitigates | T0838 | Modify Alarm Settings | attack-pattern--e5de767e-f513-41cd-aa15-33f6ce5fbf92 | technique | All field controllers should require users to authenticate for all remote or local management sessions. The authentication mechanisms should also support [Account Use Policies](https://attack.mitre.org/mitigations/M0936), [Password Policies](https://attack.mitre.org/mitigations/M0927), and [User Account Management](https://attack.mitre.org/mitigations/M0918). | relationship--03a9cdc7-3cc5-43e3-9a9c-97d1c4310e35 | 21 September 2020 | 08 March 2023
M0804 | Human User Authentication | course-of-action--66cfe23e-34b6-4583-b178-ed6a412db2b0 | mitigation | mitigates | T0821 | Modify Controller Tasking | attack-pattern--09a61657-46e1-439e-b3ed-3e4556a78243 | technique | All field controllers should require users to authenticate for all remote or local management sessions. The authentication mechanisms should also support Account Use Policies, Password Policies, and User Account Management. | relationship--5f5c38f6-aa3e-4447-a2d3-a76830ab36b0 | 25 September 2023 | 25 September 2023
M0804 | Human User Authentication | course-of-action--66cfe23e-34b6-4583-b178-ed6a412db2b0 | mitigation | mitigates | T0836 | Modify Parameter | attack-pattern--097924ce-a9a9-4039-8591-e0deedfb8722 | technique | All field controllers should require that user authenticate for all remote or local management sessions. The authentication mechanisms should also support Account Use Policies, Password Policies, and User Account Management. | relationship--af20f409-05ed-42c3-ae3e-09b047b84875 | 25 September 2023 | 25 September 2023
M0804 | Human User Authentication | course-of-action--66cfe23e-34b6-4583-b178-ed6a412db2b0 | mitigation | mitigates | T0889 | Modify Program | attack-pattern--fc5fda7e-6b2c-4457-b036-759896a2efa2 | technique | All field controllers should require users to authenticate for all remote or local management sessions. The authentication mechanisms should also support Account Use Policies, Password Policies, and User Account Management. | relationship--fad25140-73de-40d5-a010-3464188db973 | 25 September 2023 | 25 September 2023
M0804 | Human User Authentication | course-of-action--66cfe23e-34b6-4583-b178-ed6a412db2b0 | mitigation | mitigates | T0839 | Module Firmware | attack-pattern--efbf7888-f61b-4572-9c80-7e2965c60707 | technique | Devices that allow remote management of firmware should require authentication before allowing any changes. The authentication mechanisms should also support [Account Use Policies](https://attack.mitre.org/mitigations/M0936), [Password Policies](https://attack.mitre.org/mitigations/M0927), and [User Account Management](https://attack.mitre.org/mitigations/M0918). | relationship--7d6c4a00-acde-40af-bf91-a4ef009cf135 | 21 September 2020 | 08 March 2023
M0804 | Human User Authentication | course-of-action--66cfe23e-34b6-4583-b178-ed6a412db2b0 | mitigation | mitigates | T0861 | Point & Tag Identification | attack-pattern--25852363-5968-4673-b81d-341d5ed90bd1 | technique | All field controllers should require users to authenticate for all remote or local management sessions. The authentication mechanisms should also support [Account Use Policies](https://attack.mitre.org/mitigations/M0936), [Password Policies](https://attack.mitre.org/mitigations/M0927), and [User Account Management](https://attack.mitre.org/mitigations/M0918). | relationship--79324bdd-cdab-4d0a-af60-af1047c1d117 | 21 September 2020 | 08 March 2023
M0804 | Human User Authentication | course-of-action--66cfe23e-34b6-4583-b178-ed6a412db2b0 | mitigation | mitigates | T0843 | Program Download | attack-pattern--be69c571-d746-4b1f-bdd0-c0c9817e9068 | technique | All field controllers should require users to authenticate for all remote or local management sessions. The authentication mechanisms should also support [Account Use Policies](https://attack.mitre.org/mitigations/M0936), [Password Policies](https://attack.mitre.org/mitigations/M0927), and [User Account Management](https://attack.mitre.org/mitigations/M0918). | relationship--fa1bde35-63d9-4c5c-969b-2c17c29089fa | 21 September 2020 | 08 March 2023
M0804 | Human User Authentication | course-of-action--66cfe23e-34b6-4583-b178-ed6a412db2b0 | mitigation | mitigates | T0845 | Program Upload | attack-pattern--3067b85e-271e-4bc5-81ad-ab1a81d411e3 | technique | All field controllers should require users to authenticate for all remote or local management sessions. The authentication mechanisms should also support [Account Use Policies](https://attack.mitre.org/mitigations/M0936), [Password Policies](https://attack.mitre.org/mitigations/M0927), and [User Account Management](https://attack.mitre.org/mitigations/M0918). | relationship--f45c2df8-30e7-45d0-8067-7b2870767574 | 21 September 2020 | 08 March 2023
M0804 | Human User Authentication | course-of-action--66cfe23e-34b6-4583-b178-ed6a412db2b0 | mitigation | mitigates | T0886 | Remote Services | attack-pattern--e1f9cdd2-9511-4fca-90d7-f3e92cfdd0bf | technique | All remote services should require strong authentication before providing user access. | relationship--6d1906b4-e815-4688-86f1-ce61d403f8c6 | 21 September 2020 | 06 May 2022
M0804 | Human User Authentication | course-of-action--66cfe23e-34b6-4583-b178-ed6a412db2b0 | mitigation | mitigates | T0857 | System Firmware | attack-pattern--b9160e77-ea9e-4ba9-b1c8-53a3c466b13d | technique | Devices that allow remote management of firmware should require authentication before allowing any changes. The authentication mechanisms should also support [Account Use Policies](https://attack.mitre.org/mitigations/M0936), [Password Policies](https://attack.mitre.org/mitigations/M0927), and [User Account Management](https://attack.mitre.org/mitigations/M0918). | relationship--17fdec71-98e8-4314-a1be-037edede58bd | 21 September 2020 | 08 March 2023
M0935 | Limit Access to Resource Over Network | course-of-action--49b306c1-a046-42c5-a4d2-30f264ada110 | mitigation | mitigates | T0822 | External Remote Services | attack-pattern--8d2f3bab-507c-4424-b58b-edc977bd215c | technique | Limit access to remote services through centrally managed concentrators such as VPNs and other managed remote access systems. | relationship--2daeeaaa-5b4b-4bb7-a94d-78a5749027ca | 21 September 2020 | 06 May 2022
M0934 | Limit Hardware Installation | course-of-action--9e3adcad-0b8f-4ecc-a2f3-06f607f53bf0 | mitigation | mitigates | T0847 | Replication Through Removable Media | attack-pattern--c267bbee-bb59-47fe-85e0-3ed210337c21 | technique | Enforce system policies or physical restrictions to limit hardware such as USB devices on critical assets. | relationship--8f90363e-2825-4178-807f-9268a28760fa | 21 September 2020 | 06 May 2022
M0805 | Mechanical Protection Layers | course-of-action--8bc4a54e-810c-4600-8b6c-08fa8413a401 | mitigation | mitigates | T0879 | Damage to Property | attack-pattern--83ebd22f-b401-4d59-8219-2294172cf916 | technique | Protection devices should have minimal digital components to prevent exposure to related adversarial techniques. Examples include interlocks, rupture disks, release valves, etc. (Citation: A G Foord, W G Gulland, C R Howard, T Kellacher, W H Smith 2004) | relationship--e607bb66-e53f-4684-b3f1-36a997e27d01 | 21 September 2020 | 06 May 2022
M0805 | Mechanical Protection Layers | course-of-action--8bc4a54e-810c-4600-8b6c-08fa8413a401 | mitigation | mitigates | T0880 | Loss of Safety | attack-pattern--5fa00fdd-4a55-4191-94a0-564181d7fec2 | technique | Protection devices should have minimal digital components to prevent exposure to related adversarial techniques. Examples include interlocks, rupture disks, release valves, etc. (Citation: A G Foord, W G Gulland, C R Howard, T Kellacher, W H Smith 2004) | relationship--242b5a0d-e4e8-4ceb-a975-cf8efd64e981 | 21 September 2020 | 06 May 2022
M0806 | Minimize Wireless Signal Propagation | course-of-action--fce6866f-9a87-4d3e-a73c-f02d8937fe0e | mitigation | mitigates | T0860 | Wireless Compromise | attack-pattern--2877063e-1851-48d2-bcc6-bc1d2733157e | technique | Techniques can include (i) reducing transmission power on wireless signals, (ii) adjusting antenna gain to prevent extensions beyond organizational boundaries, and (iii) employing RF shielding techniques to block excessive signal propagation. (Citation: DHS National Urban Security Technology Laboratory April 2019) | relationship--b2e10e48-8bd9-472a-9c6f-1d38650e8df1 | 21 September 2020 | 06 May 2022
M0806 | Minimize Wireless Signal Propagation | course-of-action--fce6866f-9a87-4d3e-a73c-f02d8937fe0e | mitigation | mitigates | T0887 | Wireless Sniffing | attack-pattern--0fe075d5-beac-4d02-b93e-0f874997db72 | technique | Reduce the range of RF communications to their intended operating range when possible. Propagation reduction methods may include (i) reducing transmission power on wireless signals, (ii) adjusting antenna gain to prevent extensions beyond organizational boundaries, and (iii) employing RF shielding techniques to block excessive signal propagation. (Citation: DHS National Urban Security Technology Laboratory April 2019) | relationship--2f6b635b-1441-4ef0-9289-1ed6b9098d4a | 21 September 2020 | 06 May 2022
M0816 | Mitigation Limited or Not Effective | course-of-action--469b78dd-a54d-4f7c-8c3b-4a1dd916b433 | mitigation | mitigates | T0823 | Graphical User Interface | attack-pattern--b0628bfc-5376-4a38-9182-f324501cb4cf | technique | Once an adversary has access to a remote GUI they can abuse system features, such as required HMI functions. | relationship--2b62e4c0-9267-47bd-8f4d-0394b13fb566 | 21 September 2020 | 06 May 2022
M0816 | Mitigation Limited or Not Effective | course-of-action--469b78dd-a54d-4f7c-8c3b-4a1dd916b433 | mitigation | mitigates | T0877 | I/O Image | attack-pattern--53a48c74-0025-45f4-b04a-baa853df8204 | technique | This technique may not be effectively mitigated against, consider controls for assets and processes that lead to the use of this technique. | relationship--17ae41a5-cb45-4935-bec1-ea0c8bfb2f34 | 21 September 2020 | 06 May 2022
M0816 | Mitigation Limited or Not Effective | course-of-action--469b78dd-a54d-4f7c-8c3b-4a1dd916b433 | mitigation | mitigates | T0835 | Manipulate I/O Image | attack-pattern--36e9f5bc-ac13-4da4-a2f4-01f4877d9004 | technique | This technique may not be effectively mitigated against, consider controls for assets and processes that lead to the use of this technique. | relationship--b5bb5ec3-aa3c-4734-8425-4be80c5658a9 | 21 September 2020 | 06 May 2022
M0816 | Mitigation Limited or Not Effective | course-of-action--469b78dd-a54d-4f7c-8c3b-4a1dd916b433 | mitigation | mitigates | T0801 | Monitor Process State | attack-pattern--2d0d40ad-22fa-4cc8-b264-072557e1364b | technique | This type of attack technique cannot be easily mitigated with preventive controls since it is based on the abuse of system features. | relationship--5804ae3d-0daf-47a5-b026-d42878f55803 | 21 September 2020 | 06 May 2022
M0816 | Mitigation Limited or Not Effective | course-of-action--469b78dd-a54d-4f7c-8c3b-4a1dd916b433 | mitigation | mitigates | T0840 | Network Connection Enumeration | attack-pattern--ea0c980c-5cf0-43a7-a049-59c4c207566e | technique | Network connection enumeration is likely obtained by using common system tools (e.g., netstat, ipconfig). | relationship--ae7487f1-a2d0-443d-b418-cd726c5ac15f | 21 September 2020 | 06 May 2022
M0816 | Mitigation Limited or Not Effective | course-of-action--469b78dd-a54d-4f7c-8c3b-4a1dd916b433 | mitigation | mitigates | T0852 | Screen Capture | attack-pattern--c5e3cdbc-0387-4be9-8f83-ff5c0865f377 | technique | Preventing screen capture on a device may require disabling various system calls supported by the operating systems (e.g., Microsoft WindowsGraphicsCaputer APIs), however, these may be needed for other critical applications. | relationship--b5e52859-8dab-4e7e-af70-bb38c6993c98 | 21 September 2020 | 06 May 2022
M0932 | Multi-factor Authentication | course-of-action--ddf3e568-f065-49e2-9106-42029a28ddbd | mitigation | mitigates | T0822 | External Remote Services | attack-pattern--8d2f3bab-507c-4424-b58b-edc977bd215c | technique | Use strong multi-factor authentication for remote service accounts to mitigate an adversary's ability to leverage stolen credentials. Be aware of multi-factor authentication interception techniques for some implementations. | relationship--dc35c44a-a90c-48a1-8811-af2618216e42 | 21 September 2020 | 17 March 2023
M0932 | Multi-factor Authentication | course-of-action--ddf3e568-f065-49e2-9106-42029a28ddbd | mitigation | mitigates | T0842 | Network Sniffing | attack-pattern--38213338-1aab-479d-949b-c81b66ccca5c | technique | Use multi-factor authentication wherever possible. | relationship--58a0fd57-ea5f-46b0-84ac-c5b963fb7e94 | 21 September 2020 | 06 May 2022
M0932 | Multi-factor Authentication | course-of-action--ddf3e568-f065-49e2-9106-42029a28ddbd | mitigation | mitigates | T0859 | Valid Accounts | attack-pattern--cd2c76a4-5e23-4ca5-9c40-d5e0604f7101 | technique | Integrating multi-factor authentication (MFA) as part of organizational policy can greatly reduce the risk of an adversary gaining access to valid credentials that may be used for additional tactics such as initial access, lateral movement, and collecting information. MFA can also be used to restrict access to cloud resources and APIs. | relationship--9b412b1f-2dd0-4e7f-8364-f625181ba1db | 21 September 2020 | 06 May 2022
M0807 | Network Allowlists | course-of-action--aadac250-bcdc-44e3-a4ae-f52bd0a7a16a | mitigation | mitigates | T0800 | Activate Firmware Update Mode | attack-pattern--19a71d1e-6334-4233-8260-b749cae37953 | technique | Use host-based allowlists to prevent devices from accepting connections from unauthorized systems. For example, allowlists can be used to ensure devices can only connect with master stations or known management/engineering workstations. (Citation: Department of Homeland Security September 2016) | relationship--10626671-941d-4a82-a835-56059058ef87 | 21 September 2020 | 06 May 2022
M0807 | Network Allowlists | course-of-action--aadac250-bcdc-44e3-a4ae-f52bd0a7a16a | mitigation | mitigates | T0878 | Alarm Suppression | attack-pattern--2900bbd8-308a-4274-b074-5b8bde8347bc | technique | Utilize network allowlists to restrict unnecessary connections to network devices (e.g., comm servers, serial to ethernet converters) and services, especially in cases when devices have limits on the number of simultaneous sessions they support. | relationship--ade12d27-13bb-4ebf-be08-7039cf699682 | 21 September 2020 | 06 May 2022
M0807 | Network Allowlists | course-of-action--aadac250-bcdc-44e3-a4ae-f52bd0a7a16a | mitigation | mitigates | T0802 | Automated Collection | attack-pattern--3de230d4-3e42-4041-b089-17e1128feded | technique | Utilize network allowlists to restrict unnecessary connections to network devices (e.g., comm servers, serial to ethernet converters) and services, especially in cases when devices have limits on the number of simultaneous sessions they support. | relationship--6f0384e6-73c8-4fc7-bc0c-0a8c2bfa473d | 21 September 2020 | 06 May 2022
M0807 | Network Allowlists | course-of-action--aadac250-bcdc-44e3-a4ae-f52bd0a7a16a | mitigation | mitigates | T0803 | Block Command Message | attack-pattern--008b8f56-6107-48be-aa9f-746f927dbb61 | technique | Utilize network allowlists to restrict unnecessary connections to network devices (e.g., comm servers, serial to ethernet converters) and services, especially in cases when devices have limits on the number of simultaneous sessions they support. | relationship--c6562519-81c5-4eca-a815-f46ac0ed4bcc | 21 September 2020 | 06 May 2022
M0807 | Network Allowlists | course-of-action--aadac250-bcdc-44e3-a4ae-f52bd0a7a16a | mitigation | mitigates | T0804 | Block Reporting Message | attack-pattern--3f1f4ccb-9be2-4ff8-8f69-dd972221169b | technique | Utilize network allowlists to restrict unnecessary connections to network devices (e.g., comm servers, serial to ethernet converters) and services, especially in cases when devices have limits on the number of simultaneous sessions they support. | relationship--7fc9fbfc-ab9f-4189-bc1f-d473e9ef36b5 | 21 September 2020 | 06 May 2022
M0807 | Network Allowlists | course-of-action--aadac250-bcdc-44e3-a4ae-f52bd0a7a16a | mitigation | mitigates | T0805 | Block Serial COM | attack-pattern--1c478716-71d9-46a4-9a53-fa5d576adb60 | technique | Implement network allowlists to minimize serial comm port access to only authorized hosts, such as comm servers and RTUs. | relationship--cd297a7b-4b02-407e-a798-e36fef4cf3a1 | 21 September 2020 | 06 May 2022
M0807 | Network Allowlists | course-of-action--aadac250-bcdc-44e3-a4ae-f52bd0a7a16a | mitigation | mitigates | T0806 | Brute Force I/O | attack-pattern--8e7089d3-fba2-44f8-94a8-9a79c53920c4 | technique | Utilize network allowlists to restrict unnecessary connections to network devices (e.g., comm servers, serial to ethernet converters) and services, especially in cases when devices have limits on the number of simultaneous sessions they support. | relationship--461e81a2-c7ad-499e-908d-05ef2f7bd9cd | 21 September 2020 | 06 May 2022
M0807 | Network Allowlists | course-of-action--aadac250-bcdc-44e3-a4ae-f52bd0a7a16a | mitigation | mitigates | T0858 | Change Operating Mode | attack-pattern--2883c520-7957-46ca-89bd-dab1ad53b601 | technique | Use host-based allowlists to prevent devices from accepting connections from unauthorized systems. For example, allowlists can be used to ensure devices can only connect with master stations or known management/engineering workstations. (Citation: Department of Homeland Security September 2016) | relationship--ab60fe4a-5860-410a-8bca-2cdbea95e5f8 | 21 September 2020 | 06 May 2022
M0807 | Network Allowlists | course-of-action--aadac250-bcdc-44e3-a4ae-f52bd0a7a16a | mitigation | mitigates | T0884 | Connection Proxy | attack-pattern--d67adac8-e3b9-44f9-9e6d-6c2a7d69dbe4 | technique | Network allowlists can be implemented through either host-based files or system host files to specify what external connections (e.g., IP address, MAC address, port, protocol) can be made from a device. Allowlist techniques that operate at the application layer (e.g., DNP3, Modbus, HTTP) are addressed in the [Filter Network Traffic](https://attack.mitre.org/mitigations/M0937) mitigation. | relationship--c8dd2735-bd04-4413-847d-316b77c6de19 | 21 September 2020 | 08 March 2023
M0807 | Network Allowlists | course-of-action--aadac250-bcdc-44e3-a4ae-f52bd0a7a16a | mitigation | mitigates | T0879 | Damage to Property | attack-pattern--83ebd22f-b401-4d59-8219-2294172cf916 | technique | Use host-based allowlists to prevent devices from accepting connections from unauthorized systems. For example, allowlists can be used to ensure devices can only connect with master stations or known management/engineering workstations. (Citation: Department of Homeland Security September 2016) | relationship--58269882-7e8d-4d24-b7a3-dbef6196cb61 | 21 September 2020 | 06 May 2022
M0807 | Network Allowlists | course-of-action--aadac250-bcdc-44e3-a4ae-f52bd0a7a16a | mitigation | mitigates | T0868 | Detect Operating Mode | attack-pattern--2aa406ed-81c3-4c1d-ba83-cfbee5a2847a | technique | Use host-based allowlists to prevent devices from accepting connections from unauthorized systems. For example, allowlists can be used to ensure devices can only connect with master stations or known management/engineering workstations. (Citation: Department of Homeland Security September 2016) | relationship--a22fabd2-836e-4141-9219-c76cc10138ec | 21 September 2020 | 06 May 2022
M0807 | Network Allowlists | course-of-action--aadac250-bcdc-44e3-a4ae-f52bd0a7a16a | mitigation | mitigates | T0816 | Device Restart/Shutdown | attack-pattern--25dfc8ad-bd73-4dfd-84a9-3c3d383f76e9 | technique | Use host-based allowlists to prevent devices from accepting connections from unauthorized systems. For example, allowlists can be used to ensure devices can only connect with master stations or known management/engineering workstations. (Citation: Department of Homeland Security September 2016) | relationship--00e6c22b-9275-4039-b6d4-2ac0680325d6 | 21 September 2020 | 06 May 2022
M0807 | Network Allowlists | course-of-action--aadac250-bcdc-44e3-a4ae-f52bd0a7a16a | mitigation | mitigates | T0838 | Modify Alarm Settings | attack-pattern--e5de767e-f513-41cd-aa15-33f6ce5fbf92 | technique | Use host-based allowlists to prevent devices from accepting connections from unauthorized systems. For example, allowlists can be used to ensure devices can only connect with master stations or known management/engineering workstations. (Citation: Department of Homeland Security September 2016) | relationship--2cd79563-0f5a-44a1-9be4-6dc330855d64 | 21 September 2020 | 06 May 2022
M0807 | Network Allowlists | course-of-action--aadac250-bcdc-44e3-a4ae-f52bd0a7a16a | mitigation | mitigates | T0839 | Module Firmware | attack-pattern--efbf7888-f61b-4572-9c80-7e2965c60707 | technique | Use host-based allowlists to prevent devices from accepting connections from unauthorized systems. For example, allowlists can be used to ensure devices can only connect with master stations or known management/engineering workstations. (Citation: Department of Homeland Security September 2016) | relationship--f0ac1d07-fccd-4330-93cf-fbc985ee6fb9 | 21 September 2020 | 06 May 2022
M0807 | Network Allowlists | course-of-action--aadac250-bcdc-44e3-a4ae-f52bd0a7a16a | mitigation | mitigates | T0861 | Point & Tag Identification | attack-pattern--25852363-5968-4673-b81d-341d5ed90bd1 | technique | Use host-based allowlists to prevent devices from accepting connections from unauthorized systems. For example, allowlists can be used to ensure devices can only connect with master stations or known management/engineering workstations. (Citation: Department of Homeland Security September 2016) | relationship--2ecc567f-3aaa-4bd8-935f-4808d177a552 | 21 September 2020 | 06 May 2022
M0807 | Network Allowlists | course-of-action--aadac250-bcdc-44e3-a4ae-f52bd0a7a16a | mitigation | mitigates | T0843 | Program Download | attack-pattern--be69c571-d746-4b1f-bdd0-c0c9817e9068 | technique | Use host-based allowlists to prevent devices from accepting connections from unauthorized systems. For example, allowlists can be used to ensure devices can only connect with master stations or known management/engineering workstations. (Citation: Department of Homeland Security September 2016) | relationship--4256a0c2-437d-4a4c-88ac-d08d3041b8c1 | 21 September 2020 | 06 May 2022
M0807 | Network Allowlists | course-of-action--aadac250-bcdc-44e3-a4ae-f52bd0a7a16a | mitigation | mitigates | T0845 | Program Upload | attack-pattern--3067b85e-271e-4bc5-81ad-ab1a81d411e3 | technique | Use host-based allowlists to prevent devices from accepting connections from unauthorized systems. For example, allowlists can be used to ensure devices can only connect with master stations or known management/engineering workstations. (Citation: Department of Homeland Security September 2016) | relationship--c0efb24a-2329-401a-bba6-817f2867bb3f | 21 September 2020 | 06 May 2022
M0807 | Network Allowlists | course-of-action--aadac250-bcdc-44e3-a4ae-f52bd0a7a16a | mitigation | mitigates | T0886 | Remote Services | attack-pattern--e1f9cdd2-9511-4fca-90d7-f3e92cfdd0bf | technique | Network allowlists can be implemented through either host-based files or system host files to specify what external connections (e.g., IP address, MAC address, port, protocol) can be made from a device. | relationship--842a2b85-4e77-4eb6-99e1-c4a231aadf48 | 21 September 2020 | 06 May 2022
M0807 | Network Allowlists | course-of-action--aadac250-bcdc-44e3-a4ae-f52bd0a7a16a | mitigation | mitigates | T0848 | Rogue Master | attack-pattern--b14395bd-5419-4ef4-9bd8-696936f509bb | technique | Use host-based allowlists to prevent devices from accepting connections from unauthorized systems. For example, allowlists can be used to ensure devices can only connect with master stations or known management/engineering workstations. (Citation: Department of Homeland Security September 2016) | relationship--652a68a2-a26b-4e8c-86dd-fd83187ed043 | 21 September 2020 | 06 May 2022
M0807 | Network Allowlists | course-of-action--aadac250-bcdc-44e3-a4ae-f52bd0a7a16a | mitigation | mitigates | T0856 | Spoof Reporting Message | attack-pattern--8535b71e-3c12-4258-a4ab-40257a1becc4 | technique | Use host-based allowlists to prevent devices from accepting connections from unauthorized systems. For example, allowlists can be used to ensure devices can only connect with master stations or known management/engineering workstations. (Citation: Department of Homeland Security September 2016) | relationship--ce7c17b7-b60d-4ebd-9014-2c421a64d70a | 21 September 2020 | 06 May 2022
M0807 | Network Allowlists | course-of-action--aadac250-bcdc-44e3-a4ae-f52bd0a7a16a | mitigation | mitigates | T0869 | Standard Application Layer Protocol | attack-pattern--e076cca8-2f08-45c9-aff7-ea5ac798b387 | technique | Network allowlists can be implemented through either host-based files or system host files to specify what external connections (e.g., IP address, MAC address, port, protocol) can be made from a device. Allowlist techniques that operate at the application layer (e.g., DNP3, Modbus, HTTP) are addressed in the [Filter Network Traffic](https://attack.mitre.org/mitigations/M0937) mitigation. | relationship--d854cc38-adf7-485d-96b5-70606f6cb87e | 21 September 2020 | 08 March 2023
M0807 | Network Allowlists | course-of-action--aadac250-bcdc-44e3-a4ae-f52bd0a7a16a | mitigation | mitigates | T0857 | System Firmware | attack-pattern--b9160e77-ea9e-4ba9-b1c8-53a3c466b13d | technique | Use host-based allowlists to prevent devices from accepting connections from unauthorized systems. For example, allowlists can be used to ensure devices can only connect with master stations or known management/engineering workstations. (Citation: Department of Homeland Security September 2016) | relationship--3dde2b07-7c30-4a18-a9df-f85db84f9b14 | 21 September 2020 | 06 May 2022
M0807 | Network Allowlists | course-of-action--aadac250-bcdc-44e3-a4ae-f52bd0a7a16a | mitigation | mitigates | T0855 | Unauthorized Command Message | attack-pattern--40b300ba-f553-48bf-862e-9471b220d455 | technique | Use host-based allowlists to prevent devices from accepting connections from unauthorized systems. For example, allowlists can be used to ensure devices can only connect with master stations or known management/engineering workstations. (Citation: Department of Homeland Security September 2016) | relationship--b960c5ed-1ea8-4dde-9203-c02d291d3bc6 | 21 September 2020 | 06 May 2022
M0931 | Network Intrusion Prevention | course-of-action--3172222b-4983-43f7-8983-753ded4f13bc | mitigation | mitigates | T0830 | Adversary-in-the-Middle | attack-pattern--9a505987-ab05-4f46-a9a6-6441442eec3b | technique | Network intrusion detection and prevention systems that can identify traffic patterns indicative of AiTM activity can be used to mitigate activity at the network level. | relationship--b13417ea-d8da-497f-818f-d2d90562039a | 21 September 2020 | 21 March 2023
M0931 | Network Intrusion Prevention | course-of-action--3172222b-4983-43f7-8983-753ded4f13bc | mitigation | mitigates | T0885 | Commonly Used Port | attack-pattern--e6c31185-8040-4267-83d3-b217b8a92f07 | technique | Network intrusion detection and prevention systems that use network signatures to identify traffic for specific adversary malware can be used to mitigate activity at the network level. Signatures are often for unique indicators within protocols and may be based on the specific protocol used by a particular adversary or tool and will likely be different across various malware families and versions. Adversaries will likely change tool C2 signatures over time or construct protocols in such a way as to avoid detection by common defensive tools. (Citation: Gardiner, J., Cova, M., Nagaraja, S February 2014) | relationship--7dedeb73-ef90-4282-a635-cc37326773af | 21 September 2020 | 06 May 2022
M0931 | Network Intrusion Prevention | course-of-action--3172222b-4983-43f7-8983-753ded4f13bc | mitigation | mitigates | T0884 | Connection Proxy | attack-pattern--d67adac8-e3b9-44f9-9e6d-6c2a7d69dbe4 | technique | Network intrusion detection and prevention systems that use network signatures to identify traffic for specific adversary malware can be used to mitigate activity at the network level. Signatures are often for unique indicators within protocols and may be based on the specific C2 protocol used by a particular adversary or tool and will likely be different across various malware families and versions. Adversaries will likely change tool C2 signatures over time or construct protocols in such a way as to avoid detection by common defensive tools. (Citation: Gardiner, J., Cova, M., Nagaraja, S February 2014) | relationship--7411b05d-209a-4907-83ce-00ab1538fbac | 21 September 2020 | 06 May 2022
M0931 | Network Intrusion Prevention | course-of-action--3172222b-4983-43f7-8983-753ded4f13bc | mitigation | mitigates | T0867 | Lateral Tool Transfer | attack-pattern--ead7bd34-186e-4c79-9a4d-b65bcce6ed9d | technique | Network intrusion detection and prevention systems that use network signatures to identify traffic for specific adversary malware or unusual data transfer over known tools and protocols like FTP can be used to mitigate activity at the network level. Signatures are often for unique indicators within protocols and may be based on the specific obfuscation technique used by a particular adversary or tool and will likely be different across various malware families and versions. Adversaries will likely change tool C2 signatures over time or construct protocols in such a way as to avoid detection by common defensive tools. (Citation: Gardiner, J., Cova, M., Nagaraja, S February 2014) | relationship--c69eab3c-861c-45f5-8858-a595fcc7e6f6 | 21 September 2020 | 06 May 2022
M0931 | Network Intrusion Prevention | course-of-action--3172222b-4983-43f7-8983-753ded4f13bc | mitigation | mitigates | T0865 | Spearphishing Attachment | attack-pattern--648f995e-9c3a-41e4-aeee-98bb41037426 | technique | Network intrusion prevention systems and systems designed to scan and remove malicious email attachments can be used to block activity. | relationship--9a607f89-85b8-4fba-8eb7-7e4900ea693f | 21 September 2020 | 06 May 2022
M0931 | Network Intrusion Prevention | course-of-action--3172222b-4983-43f7-8983-753ded4f13bc | mitigation | mitigates | T0869 | Standard Application Layer Protocol | attack-pattern--e076cca8-2f08-45c9-aff7-ea5ac798b387 | technique | Network intrusion detection and prevention systems that use network signatures to identify traffic for specific adversary malware can be used to mitigate activity at the network level. | relationship--5be1f2b1-75fd-4e7e-901b-495cee4ab5ad | 21 September 2020 | 06 May 2022
M0931 | Network Intrusion Prevention | course-of-action--3172222b-4983-43f7-8983-753ded4f13bc | mitigation | mitigates | T0863 | User Execution | attack-pattern--2736b752-4ec5-4421-a230-8977dea7649c | technique | If a link is being visited by a user, network intrusion prevention systems and systems designed to scan and remove malicious downloads can be used to block activity. | relationship--b1d993d5-9e7e-4043-a651-07c7b5ad5a6b | 21 September 2020 | 06 May 2022
M0930 | Network Segmentation | course-of-action--1e7ccfc0-94c8-496e-8d27-032120892291 | mitigation | mitigates | T0800 | Activate Firmware Update Mode | attack-pattern--19a71d1e-6334-4233-8260-b749cae37953 | technique | Segment operational network and systems to restrict access to critical system functions to predetermined management systems. (Citation: Department of Homeland Security September 2016) | relationship--f15f24d2-e581-46ce-83e4-a924f572aae6 | 21 September 2020 | 06 May 2022
M0930 | Network Segmentation | course-of-action--1e7ccfc0-94c8-496e-8d27-032120892291 | mitigation | mitigates | T0830 | Adversary-in-the-Middle | attack-pattern--9a505987-ab05-4f46-a9a6-6441442eec3b | technique | Network segmentation can be used to isolate infrastructure components that do not require broad network access. This may mitigate, or at least alleviate, the scope of AiTM activity. | relationship--35cf6922-d48f-42ea-b7f5-f0258892bd52 | 21 September 2020 | 21 March 2023
M0930 | Network Segmentation | course-of-action--1e7ccfc0-94c8-496e-8d27-032120892291 | mitigation | mitigates | T0878 | Alarm Suppression | attack-pattern--2900bbd8-308a-4274-b074-5b8bde8347bc | technique | Segment operational assets and their management devices based on their functional role within the process. Enabling more strict isolation to more critical control and operational information within the control environment. (Citation: Karen Scarfone; Paul Hoffman September 2009) (Citation: Keith Stouffer May 2015) (Citation: Department of Homeland Security September 2016) (Citation: Dwight Anderson 2014) | relationship--b1768154-221c-48be-ab2b-549ec1eddafb | 21 September 2020 | 06 May 2022
M0930 | Network Segmentation | course-of-action--1e7ccfc0-94c8-496e-8d27-032120892291 | mitigation | mitigates | T0802 | Automated Collection | attack-pattern--3de230d4-3e42-4041-b089-17e1128feded | technique | Prevent unauthorized systems from accessing control servers or field devices containing industrial information, especially services used for common automation protocols (e.g., DNP3, OPC). | relationship--a08d85dd-a8b3-4848-94aa-941c43b6d8f2 | 21 September 2020 | 06 May 2022
M0930 | Network Segmentation | course-of-action--1e7ccfc0-94c8-496e-8d27-032120892291 | mitigation | mitigates | T0805 | Block Serial COM | attack-pattern--1c478716-71d9-46a4-9a53-fa5d576adb60 | technique | Restrict unauthorized devices from accessing serial comm ports. | relationship--51eca7b9-6330-48a8-badd-65ed3e9d3639 | 21 September 2020 | 06 May 2022
M0930 | Network Segmentation | course-of-action--1e7ccfc0-94c8-496e-8d27-032120892291 | mitigation | mitigates | T0806 | Brute Force I/O | attack-pattern--8e7089d3-fba2-44f8-94a8-9a79c53920c4 | technique | Segment operational assets and their management devices based on their functional role within the process. Enabling more strict isolation to more critical control and operational information within the control environment. (Citation: Karen Scarfone; Paul Hoffman September 2009) (Citation: Keith Stouffer May 2015) (Citation: Department of Homeland Security September 2016) (Citation: Dwight Anderson 2014) | relationship--56672ea4-cbf0-4a3e-8aed-edcc7d33133b | 21 September 2020 | 06 May 2022
M0930 | Network Segmentation | course-of-action--1e7ccfc0-94c8-496e-8d27-032120892291 | mitigation | mitigates | T0858 | Change Operating Mode | attack-pattern--2883c520-7957-46ca-89bd-dab1ad53b601 | technique | Segment operational network and systems to restrict access to critical system functions to predetermined management systems. (Citation: Department of Homeland Security September 2016) | relationship--e6e0ef82-2cb6-43fe-8f4a-b9e4d5a57b13 | 21 September 2020 | 06 May 2022
M0930 | Network Segmentation | course-of-action--1e7ccfc0-94c8-496e-8d27-032120892291 | mitigation | mitigates | T0885 | Commonly Used Port | attack-pattern--e6c31185-8040-4267-83d3-b217b8a92f07 | technique | Configure internal and external firewalls to block traffic using common ports that associate to network protocols that may be unnecessary for that particular network segment. | relationship--bde941c6-2ca0-4f94-9336-027e7eee15a1 | 21 September 2020 | 06 May 2022
M0930 | Network Segmentation | course-of-action--1e7ccfc0-94c8-496e-8d27-032120892291 | mitigation | mitigates | T0868 | Detect Operating Mode | attack-pattern--2aa406ed-81c3-4c1d-ba83-cfbee5a2847a | technique | Segment operational network and systems to restrict access to critical system functions to predetermined management systems. (Citation: Department of Homeland Security September 2016) | relationship--eac550b4-3bd2-4309-8b37-b797dd0bd8a7 | 21 September 2020 | 06 May 2022
M0930 | Network Segmentation | course-of-action--1e7ccfc0-94c8-496e-8d27-032120892291 | mitigation | mitigates | T0816 | Device Restart/Shutdown | attack-pattern--25dfc8ad-bd73-4dfd-84a9-3c3d383f76e9 | technique | Segment operational network and systems to restrict access to critical system functions to predetermined management systems. (Citation: Department of Homeland Security September 2016) | relationship--45ee1822-71e4-4d92-976d-306561b70555 | 21 September 2020 | 06 May 2022
M0930 | Network Segmentation | course-of-action--1e7ccfc0-94c8-496e-8d27-032120892291 | mitigation | mitigates | T0819 | Exploit Public-Facing Application | attack-pattern--32632a95-6856-47b9-9ab7-fea5cd7dce00 | technique | Segment externally facing servers and services from the rest of the network with a DMZ or on separate hosting infrastructure. | relationship--fcb7733f-553d-43de-a8c6-c85a5cd65041 | 21 September 2020 | 06 May 2022
M0930 | Network Segmentation | course-of-action--1e7ccfc0-94c8-496e-8d27-032120892291 | mitigation | mitigates | T0866 | Exploitation of Remote Services | attack-pattern--85a45294-08f1-4539-bf00-7da08aa7b0ee | technique | Segment networks and systems appropriately to reduce access to critical system and services communications. | relationship--63323b12-86db-4b91-a701-90daf3f98f7c | 21 September 2020 | 06 May 2022
M0930 | Network Segmentation | course-of-action--1e7ccfc0-94c8-496e-8d27-032120892291 | mitigation | mitigates | T0822 | External Remote Services | attack-pattern--8d2f3bab-507c-4424-b58b-edc977bd215c | technique | Deny direct remote access to internal systems through the use of network proxies, gateways, and firewalls. Consider a jump server or host into the DMZ for greater access control. Leverage this DMZ or corporate resources for vendor access. (Citation: Keith Stouffer May 2015) | relationship--220140ac-d927-4d86-9335-c04aa6ee3c61 | 21 September 2020 | 06 May 2022
M0930 | Network Segmentation | course-of-action--1e7ccfc0-94c8-496e-8d27-032120892291 | mitigation | mitigates | T0883 | Internet Accessible Device | attack-pattern--f8df6b57-14bc-425f-9a91-6f59f6799307 | technique | Deny direct remote access to internal systems through the use of network proxies, gateways, and firewalls. Steps should be taken to periodically inventory internet accessible devices to determine if it differs from the expected. | relationship--33215dfa-53d0-4bd7-a15d-cec9315c7c4d | 21 September 2020 | 06 May 2022
M0930 | Network Segmentation | course-of-action--1e7ccfc0-94c8-496e-8d27-032120892291 | mitigation | mitigates | T0838 | Modify Alarm Settings | attack-pattern--e5de767e-f513-41cd-aa15-33f6ce5fbf92 | technique | Segment operational network and systems to restrict access to critical system functions to predetermined management systems. (Citation: Department of Homeland Security September 2016) (Citation: N/A) | relationship--19ab6776-42de-48af-975a-568d31a3bb66 | 21 September 2020 | 06 May 2022
M0930 | Network Segmentation | course-of-action--1e7ccfc0-94c8-496e-8d27-032120892291 | mitigation | mitigates | T0839 | Module Firmware | attack-pattern--efbf7888-f61b-4572-9c80-7e2965c60707 | technique | Segment operational network and systems to restrict access to critical system functions to predetermined management systems. (Citation: Department of Homeland Security September 2016) | relationship--86d45e92-80ba-4f97-b3a3-03ad3469658b | 21 September 2020 | 06 May 2022
M0930 | Network Segmentation | course-of-action--1e7ccfc0-94c8-496e-8d27-032120892291 | mitigation | mitigates | T0842 | Network Sniffing | attack-pattern--38213338-1aab-479d-949b-c81b66ccca5c | technique | Segment networks and systems appropriately to reduce access to critical system and services communications. | relationship--34d4101b-b4c9-4ea3-a84d-81e84e7f5033 | 21 September 2020 | 06 May 2022
M0930 | Network Segmentation | course-of-action--1e7ccfc0-94c8-496e-8d27-032120892291 | mitigation | mitigates | T0861 | Point & Tag Identification | attack-pattern--25852363-5968-4673-b81d-341d5ed90bd1 | technique | Segment operational assets and their management devices based on their functional role within the process. Enabling more strict isolation to more critical control and operational information within the control environment. (Citation: Karen Scarfone; Paul Hoffman September 2009) (Citation: Keith Stouffer May 2015) (Citation: Department of Homeland Security September 2016) (Citation: Dwight Anderson 2014) | relationship--c7aac6c9-da16-46e2-8cfa-dca07a0a7562 | 21 September 2020 | 06 May 2022
M0930 | Network Segmentation | course-of-action--1e7ccfc0-94c8-496e-8d27-032120892291 | mitigation | mitigates | T0843 | Program Download | attack-pattern--be69c571-d746-4b1f-bdd0-c0c9817e9068 | technique | Segment operational network and systems to restrict access to critical system functions to predetermined management systems. (Citation: Department of Homeland Security September 2016) | relationship--8fcecf74-36df-41ab-9476-539c9ac0b339 | 21 September 2020 | 06 May 2022
M0930 | Network Segmentation | course-of-action--1e7ccfc0-94c8-496e-8d27-032120892291 | mitigation | mitigates | T0845 | Program Upload | attack-pattern--3067b85e-271e-4bc5-81ad-ab1a81d411e3 | technique | Segment operational network and systems to restrict access to critical system functions to predetermined management systems. (Citation: Department of Homeland Security September 2016) | relationship--671043a9-337f-411a-9ca9-3112e897ab09 | 21 September 2020 | 06 May 2022
M0930 | Network Segmentation | course-of-action--1e7ccfc0-94c8-496e-8d27-032120892291 | mitigation | mitigates | T0886 | Remote Services | attack-pattern--e1f9cdd2-9511-4fca-90d7-f3e92cfdd0bf | technique | Segment and control software movement between business and OT environments by way of one directional DMZs. Web access should be restricted from the OT environment. Engineering workstations, including transient cyber assets (TCAs) should have minimal connectivity to external networks, including Internet and email, further limit the extent to which these devices are dual-homed to multiple networks. (Citation: North America Transmission Forum December 2019) | relationship--502a0b7e-048a-468a-b888-e91fde47c6eb | 12 April 2021 | 06 May 2022
M0930 | Network Segmentation | course-of-action--1e7ccfc0-94c8-496e-8d27-032120892291 | mitigation | mitigates | T0848 | Rogue Master | attack-pattern--b14395bd-5419-4ef4-9bd8-696936f509bb | technique | Segment operational assets and their management devices based on their functional role within the process. Enabling more strict isolation to more critical control and operational information within the control environment. (Citation: Karen Scarfone; Paul Hoffman September 2009) (Citation: Keith Stouffer May 2015) (Citation: Department of Homeland Security September 2016) (Citation: Dwight Anderson 2014) | relationship--61668e93-6d9d-418d-9fbd-2d88c3a66544 | 21 September 2020 | 06 May 2022
M0930 | Network Segmentation | course-of-action--1e7ccfc0-94c8-496e-8d27-032120892291 | mitigation | mitigates | T0881 | Service Stop | attack-pattern--063b5b92-5361-481a-9c3f-95492ed9a2d8 | technique | Segment operational network and systems to restrict access to critical system functions to predetermined management systems. (Citation: Department of Homeland Security September 2016) | relationship--9cca3120-c95e-4f5e-bc4b-0521ab5cc512 | 21 September 2020 | 06 May 2022
M0930 | Network Segmentation | course-of-action--1e7ccfc0-94c8-496e-8d27-032120892291 | mitigation | mitigates | T0856 | Spoof Reporting Message | attack-pattern--8535b71e-3c12-4258-a4ab-40257a1becc4 | technique | Segment operational assets and their management devices based on their functional role within the process. Enabling more strict isolation to more critical control and operational information within the control environment. (Citation: Karen Scarfone; Paul Hoffman September 2009) (Citation: Keith Stouffer May 2015) (Citation: Department of Homeland Security September 2016) (Citation: Dwight Anderson 2014) | relationship--531e0589-0dad-444d-aca4-6198ba5d9fcd | 21 September 2020 | 06 May 2022
M0930 | Network Segmentation | course-of-action--1e7ccfc0-94c8-496e-8d27-032120892291 | mitigation | mitigates | T0869 | Standard Application Layer Protocol | attack-pattern--e076cca8-2f08-45c9-aff7-ea5ac798b387 | technique | Ensure proper network segmentation between higher level corporate resources and the control process environment. | relationship--0ff88ef7-44fd-4307-b381-2e0bc76ce83b | 21 September 2020 | 06 May 2022
M0930 | Network Segmentation | course-of-action--1e7ccfc0-94c8-496e-8d27-032120892291 | mitigation | mitigates | T0857 | System Firmware | attack-pattern--b9160e77-ea9e-4ba9-b1c8-53a3c466b13d | technique | Segment operational network and systems to restrict access to critical system functions to predetermined management systems. (Citation: Department of Homeland Security September 2016) | relationship--a74c14e2-eb8a-47bb-b64d-20aad9154297 | 21 September 2020 | 06 May 2022
M0930 | Network Segmentation | course-of-action--1e7ccfc0-94c8-496e-8d27-032120892291 | mitigation | mitigates | T0864 | Transient Cyber Asset | attack-pattern--35392fb4-a31d-4c6a-b9f2-1c65b7f5e6b9 | technique | Segment and control software movement between business and OT environments by way of one directional DMZs. Web access should be restricted from the OT environment. Engineering workstations, including transient cyber assets (TCAs) should have minimal connectivity to external networks, including Internet and email, further limit the extent to which these devices are dual-homed to multiple networks. (Citation: North America Transmission Forum December 2019) | relationship--798919d3-df8b-463f-b2be-4c1aa8089384 | 14 October 2021 | 06 May 2022
M0930 | Network Segmentation | course-of-action--1e7ccfc0-94c8-496e-8d27-032120892291 | mitigation | mitigates | T0855 | Unauthorized Command Message | attack-pattern--40b300ba-f553-48bf-862e-9471b220d455 | technique | Segment operational assets and their management devices based on their functional role within the process. Enabling more strict isolation to more critical control and operational information within the control environment. (Citation: Karen Scarfone; Paul Hoffman September 2009) (Citation: Keith Stouffer May 2015) (Citation: Department of Homeland Security September 2016) (Citation: Dwight Anderson 2014) | relationship--206cc4c8-797e-427b-86f1-4c81df391c6e | 21 September 2020 | 06 May 2022
M0928 | Operating System Configuration | course-of-action--9a945a29-5233-4422-a9e3-3e957b0e8bce | mitigation | mitigates | T0895 | Autorun Image | attack-pattern--77d9c726-b53e-481d-8bcc-1068aebfbb9d | technique | Configure operating systems to disable the autorun of any specific file types or drives. | relationship--98567b03-7421-4761-8caa-cbea82d89fe3 | 26 March 2024 | 26 March 2024
M0928 | Operating System Configuration | course-of-action--9a945a29-5233-4422-a9e3-3e957b0e8bce | mitigation | mitigates | T0847 | Replication Through Removable Media | attack-pattern--c267bbee-bb59-47fe-85e0-3ed210337c21 | technique | Harden the system through operating system controls to prevent the known or unknown use of malicious removable media. | relationship--604a9bf0-81a3-425b-9005-779c4f0f749d | 21 September 2020 | 06 May 2022
M0809 | Operational Information Confidentiality | course-of-action--99c746d7-a08a-4169-94f9-b8c0dad716fa | mitigation | mitigates | T0882 | Theft of Operational Information | attack-pattern--b7e13ee8-182c-4f19-92a4-a88d7d855d54 | technique | Example mitigations could include minimizing its distribution/storage or obfuscating the information (e.g., facility coverterms, codenames). In many cases this information may be necessary to support critical engineering, maintenance, or operational functions, therefore, it may not be feasible to implement. | relationship--69576d3c-d0e8-459e-9f2e-0b9c560b2e04 | 21 September 2020 | 06 May 2022
M0810 | Out-of-Band Communications Channel | course-of-action--b11cad63-ef30-4eb8-af0d-6cc46eef3f3e | mitigation | mitigates | T0830 | Adversary-in-the-Middle | attack-pattern--9a505987-ab05-4f46-a9a6-6441442eec3b | technique | Utilize out-of-band communication to validate the integrity of data from the primary channel. | relationship--52855d5d-e835-470f-a675-751c2779c861 | 21 September 2020 | 06 May 2022
M0810 | Out-of-Band Communications Channel | course-of-action--b11cad63-ef30-4eb8-af0d-6cc46eef3f3e | mitigation | mitigates | T0878 | Alarm Suppression | attack-pattern--2900bbd8-308a-4274-b074-5b8bde8347bc | technique | Provide an alternative method for alarms to be reported in the event of a communication failure. | relationship--c9395e2a-afaf-427c-bcb2-ae663d72c05c | 21 September 2020 | 06 May 2022
M0810 | Out-of-Band Communications Channel | course-of-action--b11cad63-ef30-4eb8-af0d-6cc46eef3f3e | mitigation | mitigates | T0803 | Block Command Message | attack-pattern--008b8f56-6107-48be-aa9f-746f927dbb61 | technique | Provide an alternative method for sending critical commands message to outstations, this could include using radio/cell communication to send messages to a field technician that physically performs the control function. | relationship--0c9ed09d-4ce3-4e65-845a-c21dcc5d956f | 21 September 2020 | 06 May 2022
M0810 | Out-of-Band Communications Channel | course-of-action--b11cad63-ef30-4eb8-af0d-6cc46eef3f3e | mitigation | mitigates | T0804 | Block Reporting Message | attack-pattern--3f1f4ccb-9be2-4ff8-8f69-dd972221169b | technique | Provide an alternative method for sending critical report messages to operators, this could include using radio/cell communication to obtain messages from field technicians that can locally obtain telemetry and status data. | relationship--2c8dd182-e0a1-469d-aa65-7a1f734d9b46 | 21 September 2020 | 06 May 2022
M0810 | Out-of-Band Communications Channel | course-of-action--b11cad63-ef30-4eb8-af0d-6cc46eef3f3e | mitigation | mitigates | T0805 | Block Serial COM | attack-pattern--1c478716-71d9-46a4-9a53-fa5d576adb60 | technique | Ensure devices have an alternative method for communicating in the event that a valid COM port is unavailable. | relationship--7d0ec383-4c5d-474d-9262-3f3c0d6c05b1 | 21 September 2020 | 06 May 2022
M0810 | Out-of-Band Communications Channel | course-of-action--b11cad63-ef30-4eb8-af0d-6cc46eef3f3e | mitigation | mitigates | T0813 | Denial of Control | attack-pattern--e33c7ecc-5a38-497f-beb2-a9a2049a4c20 | technique | Provide operators with redundant, out-of-band communication to support monitoring and control of the operational processes, especially when recovering from a network outage (Citation: National Institute of Standards and Technology April 2013). Out-of-band communication should utilize diverse systems and technologies to minimize common failure modes and vulnerabilities within the communications infrastructure. For example, wireless networks (e.g., 3G, 4G) can be used to provide diverse and redundant delivery of data. | relationship--2089201c-c1c6-4d92-a737-a6499e26ee7f | 21 September 2020 | 06 May 2022
M0810 | Out-of-Band Communications Channel | course-of-action--b11cad63-ef30-4eb8-af0d-6cc46eef3f3e | mitigation | mitigates | T0815 | Denial of View | attack-pattern--56ddc820-6cfb-407f-850b-52c035d123ac | technique | Provide operators with redundant, out-of-band communication to support monitoring and control of the operational processes, especially when recovering from a network outage (Citation: National Institute of Standards and Technology April 2013). Out-of-band communication should utilize diverse systems and technologies to minimize common failure modes and vulnerabilities within the communications infrastructure. For example, wireless networks (e.g., 3G, 4G) can be used to provide diverse and redundant delivery of data. | relationship--18ef2d69-d11a-4d31-a803-da989c4073f7 | 21 September 2020 | 06 May 2022
M0810 | Out-of-Band Communications Channel | course-of-action--b11cad63-ef30-4eb8-af0d-6cc46eef3f3e | mitigation | mitigates | T0826 | Loss of Availability | attack-pattern--b5b9bacb-97f2-4249-b804-47fd44de1f95 | technique | Provide operators with redundant, out-of-band communication to support monitoring and control of the operational processes, especially when recovering from a network outage (Citation: National Institute of Standards and Technology April 2013). Out-of-band communication should utilize diverse systems and technologies to minimize common failure modes and vulnerabilities within the communications infrastructure. For example, wireless networks (e.g., 3G, 4G) can be used to provide diverse and redundant delivery of data. | relationship--52c7176b-431d-44a6-8c03-7c15a8cf6ce1 | 21 September 2020 | 06 May 2022
M0810 | Out-of-Band Communications Channel | course-of-action--b11cad63-ef30-4eb8-af0d-6cc46eef3f3e | mitigation | mitigates | T0827 | Loss of Control | attack-pattern--a81696ef-c106-482c-8f80-59c30f2569fb | technique | Provide operators with redundant, out-of-band communication to support monitoring and control of the operational processes, especially when recovering from a network outage (Citation: National Institute of Standards and Technology April 2013). Out-of-band communication should utilize diverse systems and technologies to minimize common failure modes and vulnerabilities within the communications infrastructure. For example, wireless networks (e.g., 3G, 4G) can be used to provide diverse and redundant delivery of data. | relationship--8b17ad46-b0cc-4766-9cae-eba32260d468 | 21 September 2020 | 06 May 2022
M0810 | Out-of-Band Communications Channel | course-of-action--b11cad63-ef30-4eb8-af0d-6cc46eef3f3e | mitigation | mitigates | T0829 | Loss of View | attack-pattern--138979ba-0430-4de6-a128-2fc0b056ba36 | technique | Provide operators with redundant, out-of-band communication to support monitoring and control of the operational processes, especially when recovering from a network outage (Citation: National Institute of Standards and Technology April 2013). Out-of-band communication should utilize diverse systems and technologies to minimize common failure modes and vulnerabilities within the communications infrastructure. For example, wireless networks (e.g., 3G, 4G) can be used to provide diverse and redundant delivery of data. | relationship--ecf39e19-439f-4e9a-97c2-673ce4eb0a1a | 21 September 2020 | 06 May 2022
M0810 | Out-of-Band Communications Channel | course-of-action--b11cad63-ef30-4eb8-af0d-6cc46eef3f3e | mitigation | mitigates | T0831 | Manipulation of Control | attack-pattern--1af9e3fd-2bcc-414d-adbd-fe3b95c02ca1 | technique | Utilize out-of-band communication to validate the integrity of data from the primary channel. | relationship--520aad6a-2483-45bc-a172-2417137f6ca0 | 21 September 2020 | 06 May 2022
M0810 | Out-of-Band Communications Channel | course-of-action--b11cad63-ef30-4eb8-af0d-6cc46eef3f3e | mitigation | mitigates | T0832 | Manipulation of View | attack-pattern--4c2e1408-9d68-4187-8e6b-a77bc52700ec | technique | Utilize out-of-band communication to validate the integrity of data from the primary channel. | relationship--58cb4cb5-4b0f-4ce0-b3f9-5deb9de31c52 | 21 September 2020 | 06 May 2022
M0927 | Password Policies | course-of-action--5d97c693-e054-48ba-a3a3-eaf6942dfb65 | mitigation | mitigates | T0892 | Change Credential | attack-pattern--fab8fc7d-f27f-4fbb-9de6-44740aade05f | technique | Applications and appliances that utilize default username and password should be changed immediately after the installation, and before deployment to a production environment.(Citation: CISA June 2013) | relationship--53af6987-21bb-46fd-bf85-e3eeaa74de1a | 30 March 2023 | 30 March 2023
M0927 | Password Policies | course-of-action--5d97c693-e054-48ba-a3a3-eaf6942dfb65 | mitigation | mitigates | T0812 | Default Credentials | attack-pattern--8bb4538f-f16f-49f0-a431-70b5444c7349 | technique | Review vendor documents and security alerts for potentially unknown or overlooked default credentials within existing devices | relationship--33486e89-f0f4-4507-9f13-48a8f22c8ac8 | 21 September 2020 | 06 May 2022
M0927 | Password Policies | course-of-action--5d97c693-e054-48ba-a3a3-eaf6942dfb65 | mitigation | mitigates | T0822 | External Remote Services | attack-pattern--8d2f3bab-507c-4424-b58b-edc977bd215c | technique | Set and enforce secure password policies for accounts. | relationship--98f1d575-a975-42ae-8b00-2c9e22d560d5 | 21 September 2020 | 06 May 2022
M0927 | Password Policies | course-of-action--5d97c693-e054-48ba-a3a3-eaf6942dfb65 | mitigation | mitigates | T0886 | Remote Services | attack-pattern--e1f9cdd2-9511-4fca-90d7-f3e92cfdd0bf | technique | Enforce strong password requirements to prevent password brute force methods for lateral movement. | relationship--5212f36b-216f-4e32-8b64-3b4c94dfada5 | 10 April 2021 | 06 May 2022
M0927 | Password Policies | course-of-action--5d97c693-e054-48ba-a3a3-eaf6942dfb65 | mitigation | mitigates | T0859 | Valid Accounts | attack-pattern--cd2c76a4-5e23-4ca5-9c40-d5e0604f7101 | technique | Applications and appliances that utilize default username and password should be changed immediately after the installation, and before deployment to a production environment. (Citation: CISA June 2013) | relationship--a1383f2a-2ee2-47df-a661-8904a7535e0c | 21 September 2020 | 06 May 2022
M0926 | Privileged Account Management | course-of-action--622fe4d4-0e8e-4d17-9c25-6c9cef1f15d5 | mitigation | mitigates | T0809 | Data Destruction | attack-pattern--493832d9-cea6-4b63-abe7-9a65a6473675 | technique | Minimize permissions and access for service accounts to limit the information that may be impacted by malicious users or software. (Citation: National Institute of Standards and Technology April 2013) | relationship--e8eaac2d-a4bf-408f-b24f-14471db7059b | 21 September 2020 | 06 May 2022
M0926 | Privileged Account Management | course-of-action--622fe4d4-0e8e-4d17-9c25-6c9cef1f15d5 | mitigation | mitigates | T0811 | Data from Information Repositories | attack-pattern--3405891b-16aa-4bd7-bd7c-733501f9b20f | technique | Minimize permissions and access for service accounts to limit the information that may be exposed or collected by malicious users or software. (Citation: National Institute of Standards and Technology April 2013) | relationship--ba010007-6dde-4c9d-8452-69527cd1c2ba | 21 September 2020 | 06 May 2022
M0926 | Privileged Account Management | course-of-action--622fe4d4-0e8e-4d17-9c25-6c9cef1f15d5 | mitigation | mitigates | T0819 | Exploit Public-Facing Application | attack-pattern--32632a95-6856-47b9-9ab7-fea5cd7dce00 | technique | Use least privilege for service accounts. (Citation: Keith Stouffer May 2015) (Citation: National Institute of Standards and Technology April 2013) | relationship--bc3744d6-9275-4d91-8888-16d5f4d5187b | 21 September 2020 | 06 May 2022
M0926 | Privileged Account Management | course-of-action--622fe4d4-0e8e-4d17-9c25-6c9cef1f15d5 | mitigation | mitigates | T0866 | Exploitation of Remote Services | attack-pattern--85a45294-08f1-4539-bf00-7da08aa7b0ee | technique | Minimize permissions and access for service accounts to limit impact of exploitation. (Citation: Keith Stouffer May 2015) | relationship--a78e727c-8e42-448c-beb4-463804e18be0 | 21 September 2020 | 06 May 2022
M0926 | Privileged Account Management | course-of-action--622fe4d4-0e8e-4d17-9c25-6c9cef1f15d5 | mitigation | mitigates | T0842 | Network Sniffing | attack-pattern--38213338-1aab-479d-949b-c81b66ccca5c | technique | Restrict root or administrator access on user accounts to limit the ability to capture promiscuous traffic on a network through common packet capture tools. (Citation: National Institute of Standards and Technology April 2013) | relationship--26fdd07e-d194-4f8e-a9af-d5b2f1d0222e | 21 September 2020 | 06 May 2022
M0926 | Privileged Account Management | course-of-action--622fe4d4-0e8e-4d17-9c25-6c9cef1f15d5 | mitigation | mitigates | T0859 | Valid Accounts | attack-pattern--cd2c76a4-5e23-4ca5-9c40-d5e0604f7101 | technique | Audit domain and local accounts and their permission levels routinely to look for situations that could allow an adversary to gain system wide access with stolen privileged account credentials. (Citation: Microsoft May 2017) (Citation: Microsoft August 2018)These audits should also identify if default accounts have been enabled, or if new local accounts are created that have not be authorized. Follow best practices for design and administration of an enterprise network to limit privileged account use across administrative tiers. (Citation: Microsoft February 2019) | relationship--111f437a-c67d-40e4-9515-7e9b22e65eff | 21 September 2020 | 06 May 2022
M0811 | Redundancy of Service | course-of-action--f0f5c87a-a58d-440a-b3b5-ca679d98c6dd | mitigation | mitigates | T0892 | Change Credential | attack-pattern--fab8fc7d-f27f-4fbb-9de6-44740aade05f | technique | Retain cold-standby or replacement hardware of similar models to ensure continued operations of critical functions if the primary system is compromised or unavailable. (Citation: M. Rentschler and H. Heine) | relationship--cb6d67c0-33ba-4c49-ae70-d0e4f0f68794 | 30 March 2023 | 30 March 2023
M0811 | Redundancy of Service | course-of-action--f0f5c87a-a58d-440a-b3b5-ca679d98c6dd | mitigation | mitigates | T0813 | Denial of Control | attack-pattern--e33c7ecc-5a38-497f-beb2-a9a2049a4c20 | technique | Hot-standbys in diverse locations can ensure continued operations if the primarily system are compromised or unavailable. At the network layer, protocols such as the Parallel Redundancy Protocol can be used to simultaneously use redundant and diverse communication over a local network. (Citation: M. Rentschler and H. Heine) | relationship--99ec0a8e-4a4f-427c-89db-163e4b206021 | 21 September 2020 | 06 May 2022
M0811 | Redundancy of Service | course-of-action--f0f5c87a-a58d-440a-b3b5-ca679d98c6dd | mitigation | mitigates | T0815 | Denial of View | attack-pattern--56ddc820-6cfb-407f-850b-52c035d123ac | technique | Hot-standbys in diverse locations can ensure continued operations if the primarily system are compromised or unavailable. At the network layer, protocols such as the Parallel Redundancy Protocol can be used to simultaneously use redundant and diverse communication over a local network. (Citation: M. Rentschler and H. Heine) | relationship--e852e64c-b5e0-4e7f-a189-bbc7aa7932c7 | 21 September 2020 | 06 May 2022
M0811 | Redundancy of Service | course-of-action--f0f5c87a-a58d-440a-b3b5-ca679d98c6dd | mitigation | mitigates | T0826 | Loss of Availability | attack-pattern--b5b9bacb-97f2-4249-b804-47fd44de1f95 | technique | Hot-standbys in diverse locations can ensure continued operations if the primarily system is compromised or unavailable. At the network layer, protocols such as the Parallel Redundancy Protocol can be used to simultaneously use redundant and diverse communication over a local network. (Citation: M. Rentschler and H. Heine) | relationship--afb0b60e-e604-4b96-abb9-57fdce4e5108 | 21 September 2020 | 06 May 2022
M0811 | Redundancy of Service | course-of-action--f0f5c87a-a58d-440a-b3b5-ca679d98c6dd | mitigation | mitigates | T0827 | Loss of Control | attack-pattern--a81696ef-c106-482c-8f80-59c30f2569fb | technique | Hot-standbys in diverse locations can ensure continued operations if the primarily system are compromised or unavailable. At the network layer, protocols such as the Parallel Redundancy Protocol can be used to simultaneously use redundant and diverse communication over a local network. (Citation: M. Rentschler and H. Heine) | relationship--7041d8e5-3b74-402a-86b3-fd59def80632 | 21 September 2020 | 06 May 2022
M0811 | Redundancy of Service | course-of-action--f0f5c87a-a58d-440a-b3b5-ca679d98c6dd | mitigation | mitigates | T0829 | Loss of View | attack-pattern--138979ba-0430-4de6-a128-2fc0b056ba36 | technique | Hot-standbys in diverse locations can ensure continued operations if the primarily system are compromised or unavailable. At the network layer, protocols such as the Parallel Redundancy Protocol can be used to simultaneously use redundant and diverse communication over a local network. (Citation: M. Rentschler and H. Heine) | relationship--8ecf5eac-7767-411b-b54a-b374ea51b9e9 | 21 September 2020 | 06 May 2022
M0922 | Restrict File and Directory Permissions | course-of-action--f9fcb3ec-6de0-4559-8cd9-ef1c0c7d1971 | mitigation | mitigates | T0809 | Data Destruction | attack-pattern--493832d9-cea6-4b63-abe7-9a65a6473675 | technique | Protect files stored locally with proper permissions to limit opportunities for adversaries to impact data storage. (Citation: National Institute of Standards and Technology April 2013) | relationship--21b6ec9c-8779-49db-bf19-90e81893a6e4 | 21 September 2020 | 06 May 2022
M0922 | Restrict File and Directory Permissions | course-of-action--f9fcb3ec-6de0-4559-8cd9-ef1c0c7d1971 | mitigation | mitigates | T0811 | Data from Information Repositories | attack-pattern--3405891b-16aa-4bd7-bd7c-733501f9b20f | technique | Protect files with proper permissions to limit opportunities for adversaries to interact and collect information from databases. (Citation: Keith Stouffer May 2015) (Citation: National Institute of Standards and Technology April 2013) | relationship--86f1655a-db46-4d49-9051-6653da83eb13 | 21 September 2020 | 30 March 2023
M0922 | Restrict File and Directory Permissions | course-of-action--f9fcb3ec-6de0-4559-8cd9-ef1c0c7d1971 | mitigation | mitigates | T0893 | Data from Local System | attack-pattern--fa3aa267-da22-4bdd-961f-03223322a8d5 | technique | Protect files stored locally with proper permissions to limit opportunities for adversaries to interact and collect information from the local system. (Citation: Keith Stouffer May 2015) (Citation: National Institute of Standards and Technology April 2013) | relationship--94654460-b115-4056-beb1-e982ed33437b | 30 March 2023 | 30 March 2023
M0922 | Restrict File and Directory Permissions | course-of-action--f9fcb3ec-6de0-4559-8cd9-ef1c0c7d1971 | mitigation | mitigates | T0872 | Indicator Removal on Host | attack-pattern--53a26eee-1080-4d17-9762-2027d5a1b805 | technique | Protect files stored locally with proper permissions to limit opportunities for adversaries to remove indicators of their activity on the system. (Citation: Keith Stouffer May 2015) (Citation: National Institute of Standards and Technology April 2013) | relationship--92d1fd4f-6cc7-4db5-82f8-f8caa5ff59f0 | 21 September 2020 | 06 May 2022
M0922 | Restrict File and Directory Permissions | course-of-action--f9fcb3ec-6de0-4559-8cd9-ef1c0c7d1971 | mitigation | mitigates | T0849 | Masquerading | attack-pattern--ba203963-3182-41ac-af14-7e7ebc83cd61 | technique | Use file system access controls to protect system and application folders. | relationship--f703f8b2-b6b9-41f3-a551-6bb3647c45cc | 21 September 2020 | 06 May 2022
M0922 | Restrict File and Directory Permissions | course-of-action--f9fcb3ec-6de0-4559-8cd9-ef1c0c7d1971 | mitigation | mitigates | T0873 | Project File Infection | attack-pattern--e72425f8-9ae6-41d3-bfdb-e1b865e60722 | technique | Ensure permissions restrict project file access to only engineer and technician user groups and accounts. | relationship--42ab7d24-8286-4a7a-8cd7-02e54a80e13f | 21 September 2020 | 06 May 2022
M0922 | Restrict File and Directory Permissions | course-of-action--f9fcb3ec-6de0-4559-8cd9-ef1c0c7d1971 | mitigation | mitigates | T0881 | Service Stop | attack-pattern--063b5b92-5361-481a-9c3f-95492ed9a2d8 | technique | Ensure proper process and file permissions are in place to inhibit adversaries from disabling or interfering with critical services. | relationship--6833d534-9cbb-4b9f-85b6-93d3d2d6faca | 21 September 2020 | 06 May 2022
M0922 | Restrict File and Directory Permissions | course-of-action--f9fcb3ec-6de0-4559-8cd9-ef1c0c7d1971 | mitigation | mitigates | T0882 | Theft of Operational Information | attack-pattern--b7e13ee8-182c-4f19-92a4-a88d7d855d54 | technique | Protect files stored locally with proper permissions to limit opportunities for adversaries to interact and collect information from databases. (Citation: Keith Stouffer May 2015) (Citation: National Institute of Standards and Technology April 2013) | relationship--2e5f338d-92c4-4647-8fef-7c901ff774f5 | 21 September 2020 | 06 May 2022
M0944 | Restrict Library Loading | course-of-action--2ab9fc6d-3cf6-4d7b-85f1-3ad6949233b3 | mitigation | mitigates | T0874 | Hooking | attack-pattern--ab390887-afc0-4715-826d-b1b167d522ae | technique | Restrict the use of untrusted or unknown libraries, such as remote or unknown DLLs. | relationship--04882fef-2a6b-40d0-a101-da9c76a3572e | 21 September 2020 | 06 May 2022
M0924 | Restrict Registry Permissions | course-of-action--3222a807-521b-4a1a-aa13-f1cda45734b3 | mitigation | mitigates | T0881 | Service Stop | attack-pattern--063b5b92-5361-481a-9c3f-95492ed9a2d8 | technique | Ensure proper registry permissions are in place to inhibit adversaries from disabling or interfering with critical services. | relationship--0e4f272b-d744-4feb-9f3f-c24c3598538f | 21 September 2020 | 06 May 2022
M0921 | Restrict Web-Based Content | course-of-action--143b4398-3222-480a-b6a4-e131bc2d3144 | mitigation | mitigates | T0817 | Drive-by Compromise | attack-pattern--7830cfcf-b268-4ac0-a69e-73c6affbae9a | technique | Restrict browsers to limit the capabilities of malicious ads and Javascript. | relationship--fcd3fdbf-4909-48ab-85c4-ce4b34172eb0 | 21 September 2020 | 06 May 2022
M0921 | Restrict Web-Based Content | course-of-action--143b4398-3222-480a-b6a4-e131bc2d3144 | mitigation | mitigates | T0865 | Spearphishing Attachment | attack-pattern--648f995e-9c3a-41e4-aeee-98bb41037426 | technique | Consider restricting access to email within critical process environments. Additionally, downloads and attachments may be disabled if email is still necessary. | relationship--c195a0e9-d46c-487f-9a96-b138e9ca05d2 | 21 September 2020 | 06 May 2022
M0921 | Restrict Web-Based Content | course-of-action--143b4398-3222-480a-b6a4-e131bc2d3144 | mitigation | mitigates | T0863 | User Execution | attack-pattern--2736b752-4ec5-4421-a230-8977dea7649c | technique | If a link is being visited by a user, block unknown or unused files in transit by default that should not be downloaded or by policy from suspicious sites as a best practice to prevent some vectors, such as .scr, .exe, .pif, .cpl, etc. Some download scanning devices can open and analyze compressed and encrypted formats, such as zip and rar that may be used to conceal malicious files. | relationship--1aa02c37-973e-46bd-ab45-609463e514e9 | 21 September 2020 | 06 May 2022
M0920 | SSL/TLS Inspection | course-of-action--6a02e38a-9629-40c0-8c7d-e98e3470315c | mitigation | mitigates | T0884 | Connection Proxy | attack-pattern--d67adac8-e3b9-44f9-9e6d-6c2a7d69dbe4 | technique | If it is possible to inspect HTTPS traffic, the captures can be analyzed for connections that appear to be domain fronting. | relationship--20a0d820-59ef-42fc-9f56-7a93d1ce7a84 | 21 September 2020 | 06 May 2022
M0812 | Safety Instrumented Systems | course-of-action--da44255d-85c5-492c-baf3-ee823d44f848 | mitigation | mitigates | T0879 | Damage to Property | attack-pattern--83ebd22f-b401-4d59-8219-2294172cf916 | technique | Ensure that all SIS are segmented from operational networks to prevent them from being targeted by additional adversarial behavior. | relationship--d1d98f8c-aea2-4f06-9b0d-c543ed42c6a4 | 21 September 2020 | 06 May 2022
M0812 | Safety Instrumented Systems | course-of-action--da44255d-85c5-492c-baf3-ee823d44f848 | mitigation | mitigates | T0880 | Loss of Safety | attack-pattern--5fa00fdd-4a55-4191-94a0-564181d7fec2 | technique | Ensure that all SIS are segmented from operational networks to prevent them from being targeted by additional adversarial behavior. | relationship--0ffdee1a-1e83-4506-aba2-38c55812abb3 | 21 September 2020 | 06 May 2022
M0813 | Software Process and Device Authentication | course-of-action--72e46e53-e12d-4106-9c70-33241b6ed549 | mitigation | mitigates | T0800 | Activate Firmware Update Mode | attack-pattern--19a71d1e-6334-4233-8260-b749cae37953 | technique | Authenticate connections fromsoftware and devices to prevent unauthorized systems from accessing protected management functions. | relationship--758d5818-f919-4a6b-9dc2-a212595a11bd | 21 September 2020 | 21 March 2023
M0813 | Software Process and Device Authentication | course-of-action--72e46e53-e12d-4106-9c70-33241b6ed549 | mitigation | mitigates | T0830 | Adversary-in-the-Middle | attack-pattern--9a505987-ab05-4f46-a9a6-6441442eec3b | technique | To protect against AiTM, authentication mechanisms should not send credentials across the network in plaintext and should also implement mechanisms to prevent replay attacks (such as nonces or timestamps). Challenge-response based authentication techniques that do not directly send credentials over the network provide better protection from AiTM. | relationship--71e9230d-eec8-4ce1-bc96-9288bacc8b13 | 21 September 2020 | 21 March 2023
M0813 | Software Process and Device Authentication | course-of-action--72e46e53-e12d-4106-9c70-33241b6ed549 | mitigation | mitigates | T0806 | Brute Force I/O | attack-pattern--8e7089d3-fba2-44f8-94a8-9a79c53920c4 | technique | Devices should authenticate all messages between master and outstation assets. | relationship--be950e87-80ac-49ea-810a-553c7f72151b | 21 September 2020 | 06 May 2022
M0813 | Software Process and Device Authentication | course-of-action--72e46e53-e12d-4106-9c70-33241b6ed549 | mitigation | mitigates | T0858 | Change Operating Mode | attack-pattern--2883c520-7957-46ca-89bd-dab1ad53b601 | technique | Authenticate connections fromsoftware and devices to prevent unauthorized systems from accessing protected management functions. | relationship--7d5759cd-890e-4ec5-b92b-aba225d52960 | 21 September 2020 | 21 March 2023
M0813 | Software Process and Device Authentication | course-of-action--72e46e53-e12d-4106-9c70-33241b6ed549 | mitigation | mitigates | T0868 | Detect Operating Mode | attack-pattern--2aa406ed-81c3-4c1d-ba83-cfbee5a2847a | technique | Authenticate connections from software and devices to prevent unauthorized systems from accessing protected management functions. | relationship--107d9a23-991b-44f5-97f6-7f6983c7013a | 21 September 2020 | 06 May 2022
M0813 | Software Process and Device Authentication | course-of-action--72e46e53-e12d-4106-9c70-33241b6ed549 | mitigation | mitigates | T0816 | Device Restart/Shutdown | attack-pattern--25dfc8ad-bd73-4dfd-84a9-3c3d383f76e9 | technique | Authenticate connections from software and devices to prevent unauthorized systems from accessing protected management functions. | relationship--f862418a-e7b4-4783-8949-7145f3dee665 | 21 September 2020 | 06 May 2022
M0813 | Software Process and Device Authentication | course-of-action--72e46e53-e12d-4106-9c70-33241b6ed549 | mitigation | mitigates | T0838 | Modify Alarm Settings | attack-pattern--e5de767e-f513-41cd-aa15-33f6ce5fbf92 | technique | Authenticate connections fromsoftware and devices to prevent unauthorized systems from accessing protected management functions. | relationship--5d4f6aff-650c-45fe-a9d8-2080d3ea02d7 | 21 September 2020 | 21 March 2023
M0813 | Software Process and Device Authentication | course-of-action--72e46e53-e12d-4106-9c70-33241b6ed549 | mitigation | mitigates | T0839 | Module Firmware | attack-pattern--efbf7888-f61b-4572-9c80-7e2965c60707 | technique | Authenticate connections fromsoftware and devices to prevent unauthorized systems from accessing protected management functions. | relationship--26e58427-a2bd-4e77-9939-16ef60a072e7 | 21 September 2020 | 21 March 2023
M0813 | Software Process and Device Authentication | course-of-action--72e46e53-e12d-4106-9c70-33241b6ed549 | mitigation | mitigates | T0861 | Point & Tag Identification | attack-pattern--25852363-5968-4673-b81d-341d5ed90bd1 | technique | Devices should authenticate all messages between master and outstation assets. | relationship--984992e3-0407-406a-b8dd-c114d8b2d9a2 | 21 September 2020 | 06 May 2022
M0813 | Software Process and Device Authentication | course-of-action--72e46e53-e12d-4106-9c70-33241b6ed549 | mitigation | mitigates | T0843 | Program Download | attack-pattern--be69c571-d746-4b1f-bdd0-c0c9817e9068 | technique | Authenticate connections from software and devices to prevent unauthorized systems from accessing protected management functions. | relationship--028a3bcc-f299-4061-a0f2-8da85e0a3c81 | 21 September 2020 | 06 May 2022
M0813 | Software Process and Device Authentication | course-of-action--72e46e53-e12d-4106-9c70-33241b6ed549 | mitigation | mitigates | T0845 | Program Upload | attack-pattern--3067b85e-271e-4bc5-81ad-ab1a81d411e3 | technique | Authenticate connections from software and devices to prevent unauthorized systems from accessing protected management functions. | relationship--06c663f8-fcf1-47eb-ab79-284e93eafa6b | 21 September 2020 | 06 May 2022
M0813 | Software Process and Device Authentication | course-of-action--72e46e53-e12d-4106-9c70-33241b6ed549 | mitigation | mitigates | T0886 | Remote Services | attack-pattern--e1f9cdd2-9511-4fca-90d7-f3e92cfdd0bf | technique | All communication sessions to remote services should be authenticated to prevent unauthorized access. | relationship--4211c12a-57cf-4ebb-910a-6af7aa09cf34 | 12 April 2021 | 06 May 2022
M0813 | Software Process and Device Authentication | course-of-action--72e46e53-e12d-4106-9c70-33241b6ed549 | mitigation | mitigates | T0848 | Rogue Master | attack-pattern--b14395bd-5419-4ef4-9bd8-696936f509bb | technique | Devices should authenticate all messages between master and outstation assets. | relationship--0f8a6c14-1050-404a-bb6e-4fe107d5b6cd | 21 September 2020 | 06 May 2022
M0813 | Software Process and Device Authentication | course-of-action--72e46e53-e12d-4106-9c70-33241b6ed549 | mitigation | mitigates | T0856 | Spoof Reporting Message | attack-pattern--8535b71e-3c12-4258-a4ab-40257a1becc4 | technique | Devices should authenticate all messages between master and outstation assets. | relationship--088580e9-ccea-426e-9411-c1de60de650d | 21 September 2020 | 06 May 2022
M0813 | Software Process and Device Authentication | course-of-action--72e46e53-e12d-4106-9c70-33241b6ed549 | mitigation | mitigates | T0857 | System Firmware | attack-pattern--b9160e77-ea9e-4ba9-b1c8-53a3c466b13d | technique | Authenticate connections fromsoftware and devices to prevent unauthorized systems from accessing protected management functions. | relationship--bcaa4f7e-2e84-4bbb-9fb7-ca8fb003108f | 21 September 2020 | 21 March 2023
M0813 | Software Process and Device Authentication | course-of-action--72e46e53-e12d-4106-9c70-33241b6ed549 | mitigation | mitigates | T0855 | Unauthorized Command Message | attack-pattern--40b300ba-f553-48bf-862e-9471b220d455 | technique | Devices should authenticate all messages between master and outstation assets. | relationship--bbf297d3-0c3c-44be-b780-332bac17b0ba | 21 September 2020 | 06 May 2022
M0813 | Software Process and Device Authentication | course-of-action--72e46e53-e12d-4106-9c70-33241b6ed549 | mitigation | mitigates | T0860 | Wireless Compromise | attack-pattern--2877063e-1851-48d2-bcc6-bc1d2733157e | technique | Ensure wireless networks require the authentication of all devices, and that all wireless devices also authenticate network infrastructure devices (i.e., mutual authentication). For defense-in-depth purposes, utilize VPNs or ensure that application-layer protocols also authenticate the system or device. Use protocols that provide strong authentication (e.g., IEEE 802.1X), and enforce basic protections, such as MAC filtering, when stronger cryptographic techniques are not available. | relationship--3f335e8f-68da-4b06-9d96-f371ddaf23e6 | 21 September 2020 | 06 May 2022
M0814 | Static Network Configuration | course-of-action--52c7a1a9-3a78-4528-a44f-cd7b0fa3541a | mitigation | mitigates | T0830 | Adversary-in-the-Middle | attack-pattern--9a505987-ab05-4f46-a9a6-6441442eec3b | technique | Statically defined ARP entries can prevent manipulation and sniffing of switched network traffic, as some AiTM techniques depend on sending spoofed ARP messages to manipulate network host's dynamic ARP tables. | relationship--808174b7-3ab0-45b5-963e-5c10dd749e3c | 21 September 2020 | 21 March 2023
M0814 | Static Network Configuration | course-of-action--52c7a1a9-3a78-4528-a44f-cd7b0fa3541a | mitigation | mitigates | T0878 | Alarm Suppression | attack-pattern--2900bbd8-308a-4274-b074-5b8bde8347bc | technique | Unauthorized connections can be prevented by statically defining the hosts and ports used for automation protocol connections. | relationship--5d33de22-35b0-47fa-bc63-f984522340b7 | 21 September 2020 | 06 May 2022
M0814 | Static Network Configuration | course-of-action--52c7a1a9-3a78-4528-a44f-cd7b0fa3541a | mitigation | mitigates | T0803 | Block Command Message | attack-pattern--008b8f56-6107-48be-aa9f-746f927dbb61 | technique | Unauthorized connections can be prevented by statically defining the hosts and ports used for automation protocol connections. | relationship--f951d934-d555-45e9-a564-27b84518cae4 | 21 September 2020 | 06 May 2022
M0814 | Static Network Configuration | course-of-action--52c7a1a9-3a78-4528-a44f-cd7b0fa3541a | mitigation | mitigates | T0804 | Block Reporting Message | attack-pattern--3f1f4ccb-9be2-4ff8-8f69-dd972221169b | technique | Unauthorized connections can be prevented by statically defining the hosts and ports used for automation protocol connections. | relationship--139bb9e7-e5fd-4366-b2e6-4f74a73ec984 | 21 September 2020 | 06 May 2022
M0814 | Static Network Configuration | course-of-action--52c7a1a9-3a78-4528-a44f-cd7b0fa3541a | mitigation | mitigates | T0842 | Network Sniffing | attack-pattern--38213338-1aab-479d-949b-c81b66ccca5c | technique | Statically defined ARP entries can prevent manipulation and sniffing of switched network traffic, as some AiTM techniques depend on sending spoofed ARP messages to manipulate network host's dynamic ARP tables. | relationship--df6da4ec-cbe8-4f93-a41f-3726a9491938 | 21 September 2020 | 21 March 2023
M0814 | Static Network Configuration | course-of-action--52c7a1a9-3a78-4528-a44f-cd7b0fa3541a | mitigation | mitigates | T0846 | Remote System Discovery | attack-pattern--d5a69cfb-fc2a-46cb-99eb-74b236db5061 | technique | ICS environments typically have more statically defined devices, therefore minimize the use of both IT discovery protocols (e.g., DHCP, LLDP) and discovery functions in automation protocols. (Citation: D. Parsons and D. Wylie September 2019) (Citation: Colin Gray) Examples of automation protocols with discovery capabilities include OPC UA Device Discovery (Citation: Josh Rinaldi April 2016), BACnet (Citation: Aditya K Sood July 2019), and Ethernet/IP. (Citation: Langner November 2018) | relationship--b2defaaf-625d-416e-8a9d-8be6d89bacdc | 21 September 2020 | 06 May 2022
M0814 | Static Network Configuration | course-of-action--52c7a1a9-3a78-4528-a44f-cd7b0fa3541a | mitigation | mitigates | T0888 | Remote System Information Discovery | attack-pattern--2fedbe69-581f-447d-8a78-32ee7db939a9 | technique | ICS environments typically have more statically defined devices, therefore minimize the use of both IT discovery protocols (e.g., DHCP, LLDP) and discovery functions in automation protocols. (Citation: D. Parsons and D. Wylie September 2019) (Citation: Colin Gray) Examples of automation protocols with discovery capabilities include OPC UA Device Discovery (Citation: Josh Rinaldi April 2016), BACnet (Citation: Aditya K Sood July 2019), and Ethernet/IP. (Citation: Langner November 2018) | relationship--74ec9ce5-3155-488c-ae56-570c47a1d207 | 13 April 2021 | 06 May 2022
M0817 | Supply Chain Management | course-of-action--ac8f3492-7fbb-4a0a-b0b4-b75ec676136c | mitigation | mitigates | T0862 | Supply Chain Compromise | attack-pattern--5e0f75da-e108-4688-a6de-a4f07cc2cbe3 | technique | A supply chain management program should include methods the assess the trustworthiness and technical maturity of a supplier, along with technical methods (e.g., code-signing, bill of materials) needed to validate the integrity of newly obtained devices and components. Develop procurement language that emphasizes the expectations for suppliers regarding the artifacts, audit records, and technical capabilities needed to validate the integrity of the devices supply chain. (Citation: Robert A. Martin January 2021) | relationship--c8a40335-90d6-496a-b4f9-1cc93d3fffc6 | 12 April 2021 | 06 May 2022
M0919 | Threat Intelligence Program | course-of-action--d48b79b2-076d-483e-949c-0d38aa347499 | mitigation | mitigates | T0820 | Exploitation for Evasion | attack-pattern--9f947a1c-3860-48a8-8af0-a2dfa3efde03 | technique | Develop a robust cyber threat intelligence capability to determine what types and levels of threat may use software exploits and 0-days against a particular organization. | relationship--08302021-aacf-428f-a0ce-e1034d925fb0 | 21 September 2020 | 06 May 2022
M0919 | Threat Intelligence Program | course-of-action--d48b79b2-076d-483e-949c-0d38aa347499 | mitigation | mitigates | T0890 | Exploitation for Privilege Escalation | attack-pattern--cfe68e93-ce94-4c0f-a57d-3aa72cedd618 | technique | Develop a robust cyber threat intelligence capability to determine what types and levels of threat may use software exploits and 0-days against a particular organization. | relationship--f40cc6f5-111c-418f-aa84-50d920fa6c48 | 13 April 2021 | 06 May 2022
M0919 | Threat Intelligence Program | course-of-action--d48b79b2-076d-483e-949c-0d38aa347499 | mitigation | mitigates | T0866 | Exploitation of Remote Services | attack-pattern--85a45294-08f1-4539-bf00-7da08aa7b0ee | technique | Develop a robust cyber threat intelligence capability to determine what types and levels of threat may use software exploits and 0-days against a particular organization. | relationship--5914a482-dbb7-429d-96f3-77f0588ac12d | 21 September 2020 | 06 May 2022
M0951 | Update Software | course-of-action--97f33c84-8508-45b9-8a1d-cac921828c9e | mitigation | mitigates | T0817 | Drive-by Compromise | attack-pattern--7830cfcf-b268-4ac0-a69e-73c6affbae9a | technique | Ensure all browsers and plugins are kept updated to help prevent the exploit phase of this technique. Use modern browsers with security features enabled. | relationship--1a40cec9-47c3-404e-b039-b7ae83ffaf68 | 21 September 2020 | 06 May 2022
M0951 | Update Software | course-of-action--97f33c84-8508-45b9-8a1d-cac921828c9e | mitigation | mitigates | T0819 | Exploit Public-Facing Application | attack-pattern--32632a95-6856-47b9-9ab7-fea5cd7dce00 | technique | Regularly scan externally facing systems for vulnerabilities and establish procedures to rapidly patch systems when critical vulnerabilities are discovered through scanning and public disclosure. | relationship--6f2c2043-6487-467a-bb49-e8cd2509ae9f | 21 September 2020 | 06 May 2022
M0951 | Update Software | course-of-action--97f33c84-8508-45b9-8a1d-cac921828c9e | mitigation | mitigates | T0820 | Exploitation for Evasion | attack-pattern--9f947a1c-3860-48a8-8af0-a2dfa3efde03 | technique | Update software regularly by employing patch management for internal enterprise endpoints and servers. | relationship--97c5b388-518a-46ec-b2b0-41bfa6a83204 | 21 September 2020 | 06 May 2022
M0951 | Update Software | course-of-action--97f33c84-8508-45b9-8a1d-cac921828c9e | mitigation | mitigates | T0890 | Exploitation for Privilege Escalation | attack-pattern--cfe68e93-ce94-4c0f-a57d-3aa72cedd618 | technique | Update software regularly by employing patch management for internal enterprise endpoints and servers. | relationship--91f29477-2ff6-4dbf-bf68-c8825a938851 | 13 April 2021 | 06 May 2022
M0951 | Update Software | course-of-action--97f33c84-8508-45b9-8a1d-cac921828c9e | mitigation | mitigates | T0866 | Exploitation of Remote Services | attack-pattern--85a45294-08f1-4539-bf00-7da08aa7b0ee | technique | Update software regularly by employing patch management for internal enterprise endpoints and servers. | relationship--e0d101cc-1284-4e88-82d6-227fe5d19d8a | 21 September 2020 | 06 May 2022
M0951 | Update Software | course-of-action--97f33c84-8508-45b9-8a1d-cac921828c9e | mitigation | mitigates | T0862 | Supply Chain Compromise | attack-pattern--5e0f75da-e108-4688-a6de-a4f07cc2cbe3 | technique | A patch management process should be implemented to check unused dependencies, unmaintained and/or previously vulnerable dependencies, unnecessary features, components, files, and documentation. | relationship--03d44496-7a15-4e23-820f-b6f1079dbbd3 | 21 September 2020 | 06 May 2022
M0951 | Update Software | course-of-action--97f33c84-8508-45b9-8a1d-cac921828c9e | mitigation | mitigates | T0857 | System Firmware | attack-pattern--b9160e77-ea9e-4ba9-b1c8-53a3c466b13d | technique | Patch the BIOS and EFI as necessary. | relationship--a75ddacf-e87e-4a99-83f2-618486473163 | 21 September 2020 | 06 May 2022
M0951 | Update Software | course-of-action--97f33c84-8508-45b9-8a1d-cac921828c9e | mitigation | mitigates | T0864 | Transient Cyber Asset | attack-pattern--35392fb4-a31d-4c6a-b9f2-1c65b7f5e6b9 | technique | Update software on control network assets when possible. If feasible, use modern operating systems and software to reduce exposure to known vulnerabilities. | relationship--b8edcf0a-ec53-4203-b3ad-2cc734a1f1dd | 14 October 2021 | 06 May 2022
M0918 | User Account Management | course-of-action--e57ebc6d-785f-40c8-adb1-b5b5e09b3b48 | mitigation | mitigates | T0811 | Data from Information Repositories | attack-pattern--3405891b-16aa-4bd7-bd7c-733501f9b20f | technique | Ensure users and user groups have appropriate permissions for their roles through Identity and Access Management (IAM) controls to prevent misuse. Implement user accounts for each individual that may access the repositories for role enforcement and non-repudiation of actions. | relationship--b9632b4d-43c3-4bfa-88e0-629245acb8eb | 21 September 2020 | 06 May 2022
M0918 | User Account Management | course-of-action--e57ebc6d-785f-40c8-adb1-b5b5e09b3b48 | mitigation | mitigates | T0822 | External Remote Services | attack-pattern--8d2f3bab-507c-4424-b58b-edc977bd215c | technique | Consider utilizing jump boxes for external remote access. Additionally, dynamic account management may be used to easily remove accounts when not in use. | relationship--a7fbe555-a61b-4b93-bfb2-8e0dd0d6323e | 21 September 2020 | 06 May 2022
M0918 | User Account Management | course-of-action--e57ebc6d-785f-40c8-adb1-b5b5e09b3b48 | mitigation | mitigates | T0838 | Modify Alarm Settings | attack-pattern--e5de767e-f513-41cd-aa15-33f6ce5fbf92 | technique | Limit privileges of user accounts and groups so that only designated administrators or engineers can interact with alarm management and alarm configuration thresholds. | relationship--7fdaa9be-aecf-459f-b028-7c35dc8b6451 | 21 September 2020 | 06 May 2022
M0918 | User Account Management | course-of-action--e57ebc6d-785f-40c8-adb1-b5b5e09b3b48 | mitigation | mitigates | T0886 | Remote Services | attack-pattern--e1f9cdd2-9511-4fca-90d7-f3e92cfdd0bf | technique | Limit the accounts that may use remote services. Limit the permissions for accounts that are at higher risk of compromise; for example, configure SSH so users can only run specific programs. | relationship--ae10e97a-90ac-498b-8601-01081dc4af8b | 12 April 2021 | 06 May 2022
M0918 | User Account Management | course-of-action--e57ebc6d-785f-40c8-adb1-b5b5e09b3b48 | mitigation | mitigates | T0881 | Service Stop | attack-pattern--063b5b92-5361-481a-9c3f-95492ed9a2d8 | technique | Limit privileges of user accounts and groups so that only authorized administrators can change service states and configurations. | relationship--01b4a92f-da42-4dfa-8d59-53709b65940e | 21 September 2020 | 06 May 2022
M0918 | User Account Management | course-of-action--e57ebc6d-785f-40c8-adb1-b5b5e09b3b48 | mitigation | mitigates | T0859 | Valid Accounts | attack-pattern--cd2c76a4-5e23-4ca5-9c40-d5e0604f7101 | technique | Ensure users and user groups have appropriate permissions for their roles through Identity and Access Management (IAM) controls. Implement strict IAM controls to prevent access to systems except for the applications, users, and services that require access. Implement user accounts for each individual for enforcement and non-repudiation of actions. | relationship--1fc147bd-d6ab-4beb-908b-0fbe8e125b76 | 21 September 2020 | 06 May 2022
M0917 | User Training | course-of-action--dc61c280-c29d-44e5-a960-c0dd1623d2ba | mitigation | mitigates | T0811 | Data from Information Repositories | attack-pattern--3405891b-16aa-4bd7-bd7c-733501f9b20f | technique | Develop and publish policies that define acceptable information to be stored in repositories. | relationship--f497fd3e-8f05-4db2-97cc-48a8d35a8827 | 21 September 2020 | 06 May 2022
M0917 | User Training | course-of-action--dc61c280-c29d-44e5-a960-c0dd1623d2ba | mitigation | mitigates | T0893 | Data from Local System | attack-pattern--fa3aa267-da22-4bdd-961f-03223322a8d5 | technique | Develop and publish policies that define acceptable information to be stored on local systems. | relationship--b48a9fea-26a5-473c-9a5d-fcc3531e1fd3 | 30 March 2023 | 30 March 2023
M0917 | User Training | course-of-action--dc61c280-c29d-44e5-a960-c0dd1623d2ba | mitigation | mitigates | T0865 | Spearphishing Attachment | attack-pattern--648f995e-9c3a-41e4-aeee-98bb41037426 | technique | Users can be trained to identify social engineering techniques and spearphishing emails. | relationship--81ca994a-b350-424d-8f39-a0b64aa76260 | 21 September 2020 | 06 May 2022
M0917 | User Training | course-of-action--dc61c280-c29d-44e5-a960-c0dd1623d2ba | mitigation | mitigates | T0863 | User Execution | attack-pattern--2736b752-4ec5-4421-a230-8977dea7649c | technique | Use user training as a way to bring awareness to common phishing and spearphishing techniques and how to raise suspicion for potentially malicious events. | relationship--71c9db9c-6f0c-4e33-a20a-dcd5b791a49a | 21 September 2020 | 06 May 2022
M0818 | Validate Program Inputs | course-of-action--1cbcceef-3233-4062-aa86-ec91afe39517 | mitigation | mitigates | T0836 | Modify Parameter | attack-pattern--097924ce-a9a9-4039-8591-e0deedfb8722 | technique | Devices and programs should validate the content of any remote parameter changes, including those from HMIs, control servers, or engineering workstations.(Citation: PLCTop20 Mar 2023) | relationship--f86bde61-c4ec-4d40-9768-32e9b52c1702 | 22 March 2023 | 22 March 2023
M0818 | Validate Program Inputs | course-of-action--1cbcceef-3233-4062-aa86-ec91afe39517 | mitigation | mitigates | T0855 | Unauthorized Command Message | attack-pattern--40b300ba-f553-48bf-862e-9471b220d455 | technique | Devices and programs that receive command messages from remote systems (e.g., control servers) should verify those commands before taking any actions on them. | relationship--07c0e166-f05e-413f-8f3e-f487317c9626 | 22 March 2023 | 22 March 2023
M0916 | Vulnerability Scanning | course-of-action--de0bc375-50e1-4e26-a342-a8ff8c9d3037 | mitigation | mitigates | T0819 | Exploit Public-Facing Application | attack-pattern--32632a95-6856-47b9-9ab7-fea5cd7dce00 | technique | Regularly scan externally facing systems for vulnerabilities and establish procedures to rapidly patch systems when critical vulnerabilities are discovered through scanning and public disclosure. | relationship--968830b7-ee80-4a6e-96a4-9fc70470e4a9 | 21 September 2020 | 06 May 2022
M0916 | Vulnerability Scanning | course-of-action--de0bc375-50e1-4e26-a342-a8ff8c9d3037 | mitigation | mitigates | T0866 | Exploitation of Remote Services | attack-pattern--85a45294-08f1-4539-bf00-7da08aa7b0ee | technique | Regularly scan the internal network for available services to identify new and potentially vulnerable services. | relationship--1f87378c-49fb-4da5-8ed3-3672633d3713 | 21 September 2020 | 06 May 2022
M0916 | Vulnerability Scanning | course-of-action--de0bc375-50e1-4e26-a342-a8ff8c9d3037 | mitigation | mitigates | T0862 | Supply Chain Compromise | attack-pattern--5e0f75da-e108-4688-a6de-a4f07cc2cbe3 | technique | Implement continuous monitoring of vulnerability sources. Also, use automatic and manual code review tools. (Citation: OWASP) | relationship--c67e3535-69a9-4234-8170-4ad6efc632b7 | 21 September 2020 | 06 May 2022
M0815 | Watchdog Timers | course-of-action--98aa0d61-fc9d-4b2d-8f18-b25d03549f53 | mitigation | mitigates | T0814 | Denial of Service | attack-pattern--1b22b676-9347-4c55-9a35-ef0dc653db5b | technique | System and process restarts should be performed when a timeout condition occurs. | relationship--5d0a7979-0420-4fd1-b5ad-cb5565cbdf9d | 21 September 2020 | 06 May 2022

## targeted assets
source ID | source name | source ref | source type | mapping type | target ID | target name | target ref | target type | mapping description | STIX ID | created | last modified
T0800 | Activate Firmware Update Mode | attack-pattern--19a71d1e-6334-4233-8260-b749cae37953 | technique | targets | A0009 | Data Gateway | x-mitre-asset--68388d4f-8138-420b-be2b-5a7dfe9ff6b4 | asset |  | relationship--128de3f9-df58-4122-9523-0ac65a6ebf71 | 29 September 2023 | 29 September 2023
T0800 | Activate Firmware Update Mode | attack-pattern--19a71d1e-6334-4233-8260-b749cae37953 | technique | targets | A0013 | Field I/O | x-mitre-asset--2b676abd-8263-49ea-81a4-78a7e1f776fe | asset |  | relationship--e5c9aacb-51e3-41d3-995d-9e6ed04a2454 | 02 October 2023 | 02 October 2023
T0800 | Activate Firmware Update Mode | attack-pattern--19a71d1e-6334-4233-8260-b749cae37953 | technique | targets | A0002 | Human-Machine Interface (HMI) | x-mitre-asset--3a95f7e4-4877-4967-b2e8-e287976c3e64 | asset |  | relationship--0dbf48f3-4579-4ca2-aceb-19d3e0449136 | 29 September 2023 | 29 September 2023
T0800 | Activate Firmware Update Mode | attack-pattern--19a71d1e-6334-4233-8260-b749cae37953 | technique | targets | A0005 | Intelligent Electronic Device (IED) | x-mitre-asset--75f810ad-b678-4c57-b93b-fdc79bba0c04 | asset |  | relationship--c4b036ee-be86-48cb-9f01-ab8f78e5bb37 | 28 September 2023 | 28 September 2023
T0800 | Activate Firmware Update Mode | attack-pattern--19a71d1e-6334-4233-8260-b749cae37953 | technique | targets | A0003 | Programmable Logic Controller (PLC) | x-mitre-asset--986c455b-0f43-42b6-8360-33ac48bd9990 | asset |  | relationship--f9907fb1-976b-4f51-ac13-b45f2ff9452b | 28 September 2023 | 28 September 2023
T0800 | Activate Firmware Update Mode | attack-pattern--19a71d1e-6334-4233-8260-b749cae37953 | technique | targets | A0004 | Remote Terminal Unit (RTU) | x-mitre-asset--1769c499-55e5-462f-bab2-c39b8cd5ae32 | asset |  | relationship--ba943eeb-5673-44b5-acbf-1cddc2fefb1a | 28 September 2023 | 28 September 2023
T0800 | Activate Firmware Update Mode | attack-pattern--19a71d1e-6334-4233-8260-b749cae37953 | technique | targets | A0010 | Safety Controller | x-mitre-asset--69d1b1ef-e918-4cfd-9a98-29debd04cb32 | asset |  | relationship--b59a96e4-bd70-4459-9609-66563bccd9c3 | 29 September 2023 | 29 September 2023
T0830 | Adversary-in-the-Middle | attack-pattern--9a505987-ab05-4f46-a9a6-6441442eec3b | technique | targets | A0008 | Application Server | x-mitre-asset--973bc51e-c41e-4cec-ac03-9389c71f3d0d | asset |  | relationship--69cf4015-fae1-47f6-9253-1f99209288a5 | 29 September 2023 | 29 September 2023
T0830 | Adversary-in-the-Middle | attack-pattern--9a505987-ab05-4f46-a9a6-6441442eec3b | technique | targets | A0007 | Control Server | x-mitre-asset--ecb81a8b-022e-4529-a404-55cffca7d3a3 | asset |  | relationship--da987131-bf37-4730-9914-323879d2b5c3 | 28 September 2023 | 28 September 2023
T0830 | Adversary-in-the-Middle | attack-pattern--9a505987-ab05-4f46-a9a6-6441442eec3b | technique | targets | A0009 | Data Gateway | x-mitre-asset--68388d4f-8138-420b-be2b-5a7dfe9ff6b4 | asset |  | relationship--ab844cd2-0f56-44f9-9838-cd5f04d75f3e | 29 September 2023 | 29 September 2023
T0830 | Adversary-in-the-Middle | attack-pattern--9a505987-ab05-4f46-a9a6-6441442eec3b | technique | targets | A0006 | Data Historian | x-mitre-asset--e2c3336a-dd93-44d6-8246-f93cf132c499 | asset |  | relationship--327f65bc-8a33-4dbb-88d4-714a9e42442b | 28 September 2023 | 28 September 2023
T0830 | Adversary-in-the-Middle | attack-pattern--9a505987-ab05-4f46-a9a6-6441442eec3b | technique | targets | A0013 | Field I/O | x-mitre-asset--2b676abd-8263-49ea-81a4-78a7e1f776fe | asset |  | relationship--eb5310c6-7500-4b16-8ca7-6678c6232001 | 29 September 2023 | 29 September 2023
T0830 | Adversary-in-the-Middle | attack-pattern--9a505987-ab05-4f46-a9a6-6441442eec3b | technique | targets | A0002 | Human-Machine Interface (HMI) | x-mitre-asset--3a95f7e4-4877-4967-b2e8-e287976c3e64 | asset |  | relationship--745b5268-f2b3-499c-a6a4-63d7e8667ff7 | 29 September 2023 | 29 September 2023
T0830 | Adversary-in-the-Middle | attack-pattern--9a505987-ab05-4f46-a9a6-6441442eec3b | technique | targets | A0005 | Intelligent Electronic Device (IED) | x-mitre-asset--75f810ad-b678-4c57-b93b-fdc79bba0c04 | asset |  | relationship--01335508-22bb-4185-a7e2-49ec9bee6423 | 28 September 2023 | 28 September 2023
T0830 | Adversary-in-the-Middle | attack-pattern--9a505987-ab05-4f46-a9a6-6441442eec3b | technique | targets | A0012 | Jump Host | x-mitre-asset--14932ed5-1098-4cc1-9f57-159ab7366787 | asset |  | relationship--0a421699-f013-49f4-9d9f-01d95d210510 | 28 September 2023 | 28 September 2023
T0830 | Adversary-in-the-Middle | attack-pattern--9a505987-ab05-4f46-a9a6-6441442eec3b | technique | targets | A0003 | Programmable Logic Controller (PLC) | x-mitre-asset--986c455b-0f43-42b6-8360-33ac48bd9990 | asset |  | relationship--df80e2b6-5672-4f26-a19c-a394f3731f24 | 28 September 2023 | 28 September 2023
T0830 | Adversary-in-the-Middle | attack-pattern--9a505987-ab05-4f46-a9a6-6441442eec3b | technique | targets | A0004 | Remote Terminal Unit (RTU) | x-mitre-asset--1769c499-55e5-462f-bab2-c39b8cd5ae32 | asset |  | relationship--eebae2f3-aaa1-4410-8b75-db5bdac1d4d6 | 28 September 2023 | 28 September 2023
T0830 | Adversary-in-the-Middle | attack-pattern--9a505987-ab05-4f46-a9a6-6441442eec3b | technique | targets | A0014 | Routers | x-mitre-asset--dcb1d1c1-b195-45bf-b4cf-5b98c5b859a5 | asset |  | relationship--02117d44-46d2-41f0-a5fb-ba303e6ee124 | 29 September 2023 | 29 September 2023
T0830 | Adversary-in-the-Middle | attack-pattern--9a505987-ab05-4f46-a9a6-6441442eec3b | technique | targets | A0010 | Safety Controller | x-mitre-asset--69d1b1ef-e918-4cfd-9a98-29debd04cb32 | asset |  | relationship--79235599-e23f-43cb-9c56-1eb22b7c4664 | 29 September 2023 | 29 September 2023
T0830 | Adversary-in-the-Middle | attack-pattern--9a505987-ab05-4f46-a9a6-6441442eec3b | technique | targets | A0011 | Virtual Private Network (VPN) Server | x-mitre-asset--0804f037-a3b9-4715-98e1-9f73d19d6945 | asset |  | relationship--8fe2bc4c-e9f7-430d-84d5-e3d603141dcb | 29 September 2023 | 29 September 2023
T0830 | Adversary-in-the-Middle | attack-pattern--9a505987-ab05-4f46-a9a6-6441442eec3b | technique | targets | A0001 | Workstation | x-mitre-asset--f1315d02-9118-4e3b-8cdf-4c2d3f77ce41 | asset |  | relationship--a91295dc-b381-4dc9-9384-9f9949066778 | 29 September 2023 | 29 September 2023
T0878 | Alarm Suppression | attack-pattern--2900bbd8-308a-4274-b074-5b8bde8347bc | technique | targets | A0007 | Control Server | x-mitre-asset--ecb81a8b-022e-4529-a404-55cffca7d3a3 | asset |  | relationship--305866af-1f36-49e0-a57d-d5faaf29011c | 28 September 2023 | 28 September 2023
T0878 | Alarm Suppression | attack-pattern--2900bbd8-308a-4274-b074-5b8bde8347bc | technique | targets | A0009 | Data Gateway | x-mitre-asset--68388d4f-8138-420b-be2b-5a7dfe9ff6b4 | asset |  | relationship--11a82651-4d69-4738-89c6-17d0243cbbb0 | 29 September 2023 | 29 September 2023
T0878 | Alarm Suppression | attack-pattern--2900bbd8-308a-4274-b074-5b8bde8347bc | technique | targets | A0006 | Data Historian | x-mitre-asset--e2c3336a-dd93-44d6-8246-f93cf132c499 | asset |  | relationship--b0945f9b-5608-472e-ad70-7b42c3e062a1 | 28 September 2023 | 28 September 2023
T0878 | Alarm Suppression | attack-pattern--2900bbd8-308a-4274-b074-5b8bde8347bc | technique | targets | A0002 | Human-Machine Interface (HMI) | x-mitre-asset--3a95f7e4-4877-4967-b2e8-e287976c3e64 | asset |  | relationship--0ef1e408-8ebb-4b28-b619-02914b7bae29 | 29 September 2023 | 29 September 2023
T0878 | Alarm Suppression | attack-pattern--2900bbd8-308a-4274-b074-5b8bde8347bc | technique | targets | A0005 | Intelligent Electronic Device (IED) | x-mitre-asset--75f810ad-b678-4c57-b93b-fdc79bba0c04 | asset |  | relationship--45d14170-7f7b-4e08-b53f-42fa4a3a04d9 | 28 September 2023 | 28 September 2023
T0878 | Alarm Suppression | attack-pattern--2900bbd8-308a-4274-b074-5b8bde8347bc | technique | targets | A0003 | Programmable Logic Controller (PLC) | x-mitre-asset--986c455b-0f43-42b6-8360-33ac48bd9990 | asset |  | relationship--b3aab26c-09c6-4264-af2a-5df260d3d8e2 | 28 September 2023 | 28 September 2023
T0878 | Alarm Suppression | attack-pattern--2900bbd8-308a-4274-b074-5b8bde8347bc | technique | targets | A0004 | Remote Terminal Unit (RTU) | x-mitre-asset--1769c499-55e5-462f-bab2-c39b8cd5ae32 | asset |  | relationship--9ffbf620-8e1f-4542-a271-9a3692db9a47 | 28 September 2023 | 28 September 2023
T0878 | Alarm Suppression | attack-pattern--2900bbd8-308a-4274-b074-5b8bde8347bc | technique | targets | A0010 | Safety Controller | x-mitre-asset--69d1b1ef-e918-4cfd-9a98-29debd04cb32 | asset |  | relationship--76537fd7-5782-4a8d-9b54-117b168a4306 | 29 September 2023 | 29 September 2023
T0802 | Automated Collection | attack-pattern--3de230d4-3e42-4041-b089-17e1128feded | technique | targets | A0007 | Control Server | x-mitre-asset--ecb81a8b-022e-4529-a404-55cffca7d3a3 | asset |  | relationship--544e996c-0bdc-42b2-91af-14c27d4213b9 | 28 September 2023 | 28 September 2023
T0802 | Automated Collection | attack-pattern--3de230d4-3e42-4041-b089-17e1128feded | technique | targets | A0006 | Data Historian | x-mitre-asset--e2c3336a-dd93-44d6-8246-f93cf132c499 | asset |  | relationship--ff107632-751b-4efb-86bd-af670b48d35d | 28 September 2023 | 28 September 2023
T0802 | Automated Collection | attack-pattern--3de230d4-3e42-4041-b089-17e1128feded | technique | targets | A0003 | Programmable Logic Controller (PLC) | x-mitre-asset--986c455b-0f43-42b6-8360-33ac48bd9990 | asset |  | relationship--685249f9-e51a-4914-8b7f-09679e04198b | 28 September 2023 | 28 September 2023
T0895 | Autorun Image | attack-pattern--77d9c726-b53e-481d-8bcc-1068aebfbb9d | technique | targets | A0008 | Application Server | x-mitre-asset--973bc51e-c41e-4cec-ac03-9389c71f3d0d | asset |  | relationship--630eb861-eb37-4258-9dbd-87789df2257a | 26 March 2024 | 26 March 2024
T0895 | Autorun Image | attack-pattern--77d9c726-b53e-481d-8bcc-1068aebfbb9d | technique | targets | A0007 | Control Server | x-mitre-asset--ecb81a8b-022e-4529-a404-55cffca7d3a3 | asset |  | relationship--fd309395-8fcc-402c-9227-90ac897fd602 | 26 March 2024 | 26 March 2024
T0895 | Autorun Image | attack-pattern--77d9c726-b53e-481d-8bcc-1068aebfbb9d | technique | targets | A0006 | Data Historian | x-mitre-asset--e2c3336a-dd93-44d6-8246-f93cf132c499 | asset |  | relationship--982d0b4f-274a-4738-9262-57fc80d468f9 | 26 March 2024 | 26 March 2024
T0895 | Autorun Image | attack-pattern--77d9c726-b53e-481d-8bcc-1068aebfbb9d | technique | targets | A0002 | Human-Machine Interface (HMI) | x-mitre-asset--3a95f7e4-4877-4967-b2e8-e287976c3e64 | asset |  | relationship--fcba6a58-72b0-4d54-a887-740624e22f6f | 26 March 2024 | 26 March 2024
T0895 | Autorun Image | attack-pattern--77d9c726-b53e-481d-8bcc-1068aebfbb9d | technique | targets | A0012 | Jump Host | x-mitre-asset--14932ed5-1098-4cc1-9f57-159ab7366787 | asset |  | relationship--a72c212f-6d4f-4c5d-873d-afa42021024c | 26 March 2024 | 26 March 2024
T0895 | Autorun Image | attack-pattern--77d9c726-b53e-481d-8bcc-1068aebfbb9d | technique | targets | A0001 | Workstation | x-mitre-asset--f1315d02-9118-4e3b-8cdf-4c2d3f77ce41 | asset |  | relationship--6eafa3e9-f53f-43b5-ac24-1415b05b537f | 26 March 2024 | 26 March 2024
T0803 | Block Command Message | attack-pattern--008b8f56-6107-48be-aa9f-746f927dbb61 | technique | targets | A0007 | Control Server | x-mitre-asset--ecb81a8b-022e-4529-a404-55cffca7d3a3 | asset |  | relationship--788a2994-f3fd-4ac4-9ef3-06a72a4e1631 | 28 September 2023 | 28 September 2023
T0803 | Block Command Message | attack-pattern--008b8f56-6107-48be-aa9f-746f927dbb61 | technique | targets | A0013 | Field I/O | x-mitre-asset--2b676abd-8263-49ea-81a4-78a7e1f776fe | asset |  | relationship--17d5794d-dcd5-4e0f-87e4-87d41c24b5fa | 02 October 2023 | 02 October 2023
T0803 | Block Command Message | attack-pattern--008b8f56-6107-48be-aa9f-746f927dbb61 | technique | targets | A0002 | Human-Machine Interface (HMI) | x-mitre-asset--3a95f7e4-4877-4967-b2e8-e287976c3e64 | asset |  | relationship--a46f722e-4399-4aa6-b0a9-61fae9d0bf63 | 29 September 2023 | 29 September 2023
T0803 | Block Command Message | attack-pattern--008b8f56-6107-48be-aa9f-746f927dbb61 | technique | targets | A0005 | Intelligent Electronic Device (IED) | x-mitre-asset--75f810ad-b678-4c57-b93b-fdc79bba0c04 | asset |  | relationship--0951222a-42d1-4635-bb12-5285bc6500e0 | 28 September 2023 | 28 September 2023
T0803 | Block Command Message | attack-pattern--008b8f56-6107-48be-aa9f-746f927dbb61 | technique | targets | A0003 | Programmable Logic Controller (PLC) | x-mitre-asset--986c455b-0f43-42b6-8360-33ac48bd9990 | asset |  | relationship--8f947e00-2579-4120-a8b0-d466e59fac1a | 28 September 2023 | 28 September 2023
T0803 | Block Command Message | attack-pattern--008b8f56-6107-48be-aa9f-746f927dbb61 | technique | targets | A0004 | Remote Terminal Unit (RTU) | x-mitre-asset--1769c499-55e5-462f-bab2-c39b8cd5ae32 | asset |  | relationship--9a3e771d-d84f-4f2a-baf9-4478abdbdbcf | 28 September 2023 | 28 September 2023
T0803 | Block Command Message | attack-pattern--008b8f56-6107-48be-aa9f-746f927dbb61 | technique | targets | A0010 | Safety Controller | x-mitre-asset--69d1b1ef-e918-4cfd-9a98-29debd04cb32 | asset |  | relationship--5677e801-bd49-404b-b54a-6b00da52530c | 29 September 2023 | 29 September 2023
T0804 | Block Reporting Message | attack-pattern--3f1f4ccb-9be2-4ff8-8f69-dd972221169b | technique | targets | A0007 | Control Server | x-mitre-asset--ecb81a8b-022e-4529-a404-55cffca7d3a3 | asset |  | relationship--86e7a6d1-baa5-4a8d-9ba8-302fb0d72f9c | 28 September 2023 | 28 September 2023
T0804 | Block Reporting Message | attack-pattern--3f1f4ccb-9be2-4ff8-8f69-dd972221169b | technique | targets | A0009 | Data Gateway | x-mitre-asset--68388d4f-8138-420b-be2b-5a7dfe9ff6b4 | asset |  | relationship--afe18ec4-b5b8-43f7-b9e9-64a579b4b4e1 | 29 September 2023 | 29 September 2023
T0804 | Block Reporting Message | attack-pattern--3f1f4ccb-9be2-4ff8-8f69-dd972221169b | technique | targets | A0013 | Field I/O | x-mitre-asset--2b676abd-8263-49ea-81a4-78a7e1f776fe | asset |  | relationship--31d7e048-92fc-4b63-b0d5-28b64b39797a | 02 October 2023 | 02 October 2023
T0804 | Block Reporting Message | attack-pattern--3f1f4ccb-9be2-4ff8-8f69-dd972221169b | technique | targets | A0002 | Human-Machine Interface (HMI) | x-mitre-asset--3a95f7e4-4877-4967-b2e8-e287976c3e64 | asset |  | relationship--4f4e2e9e-6f9a-4c9c-af2b-4db4ec444c93 | 29 September 2023 | 29 September 2023
T0804 | Block Reporting Message | attack-pattern--3f1f4ccb-9be2-4ff8-8f69-dd972221169b | technique | targets | A0005 | Intelligent Electronic Device (IED) | x-mitre-asset--75f810ad-b678-4c57-b93b-fdc79bba0c04 | asset |  | relationship--cd54b7ba-c96c-49c8-90d2-15677efb8fe2 | 28 September 2023 | 28 September 2023
T0804 | Block Reporting Message | attack-pattern--3f1f4ccb-9be2-4ff8-8f69-dd972221169b | technique | targets | A0003 | Programmable Logic Controller (PLC) | x-mitre-asset--986c455b-0f43-42b6-8360-33ac48bd9990 | asset |  | relationship--483719ad-c973-4210-b059-14e87dbd45f8 | 28 September 2023 | 28 September 2023
T0804 | Block Reporting Message | attack-pattern--3f1f4ccb-9be2-4ff8-8f69-dd972221169b | technique | targets | A0004 | Remote Terminal Unit (RTU) | x-mitre-asset--1769c499-55e5-462f-bab2-c39b8cd5ae32 | asset |  | relationship--908e3fa1-e2b9-475e-b72d-06343a65a3c6 | 28 September 2023 | 28 September 2023
T0804 | Block Reporting Message | attack-pattern--3f1f4ccb-9be2-4ff8-8f69-dd972221169b | technique | targets | A0010 | Safety Controller | x-mitre-asset--69d1b1ef-e918-4cfd-9a98-29debd04cb32 | asset |  | relationship--eff19f74-4940-4c8e-a3b3-b3c16fe3f5e0 | 29 September 2023 | 29 September 2023
T0805 | Block Serial COM | attack-pattern--1c478716-71d9-46a4-9a53-fa5d576adb60 | technique | targets | A0007 | Control Server | x-mitre-asset--ecb81a8b-022e-4529-a404-55cffca7d3a3 | asset |  | relationship--4ad48410-efd9-41c0-ac59-e4343d3b9198 | 28 September 2023 | 28 September 2023
T0805 | Block Serial COM | attack-pattern--1c478716-71d9-46a4-9a53-fa5d576adb60 | technique | targets | A0009 | Data Gateway | x-mitre-asset--68388d4f-8138-420b-be2b-5a7dfe9ff6b4 | asset |  | relationship--ab5c9a38-3140-43b6-bcf4-6197a116cd0b | 29 September 2023 | 29 September 2023
T0805 | Block Serial COM | attack-pattern--1c478716-71d9-46a4-9a53-fa5d576adb60 | technique | targets | A0013 | Field I/O | x-mitre-asset--2b676abd-8263-49ea-81a4-78a7e1f776fe | asset |  | relationship--6b54f354-9059-4366-8077-87360c4db2ab | 02 October 2023 | 02 October 2023
T0805 | Block Serial COM | attack-pattern--1c478716-71d9-46a4-9a53-fa5d576adb60 | technique | targets | A0002 | Human-Machine Interface (HMI) | x-mitre-asset--3a95f7e4-4877-4967-b2e8-e287976c3e64 | asset |  | relationship--edfa4bcb-6304-42df-b7c6-8caf480c66f2 | 29 September 2023 | 29 September 2023
T0805 | Block Serial COM | attack-pattern--1c478716-71d9-46a4-9a53-fa5d576adb60 | technique | targets | A0005 | Intelligent Electronic Device (IED) | x-mitre-asset--75f810ad-b678-4c57-b93b-fdc79bba0c04 | asset |  | relationship--66738beb-0a33-4d70-baec-8307b5b34f80 | 28 September 2023 | 28 September 2023
T0805 | Block Serial COM | attack-pattern--1c478716-71d9-46a4-9a53-fa5d576adb60 | technique | targets | A0012 | Jump Host | x-mitre-asset--14932ed5-1098-4cc1-9f57-159ab7366787 | asset |  | relationship--9ba76ea3-9ebb-49d7-803a-5cf2deef6875 | 28 September 2023 | 28 September 2023
T0805 | Block Serial COM | attack-pattern--1c478716-71d9-46a4-9a53-fa5d576adb60 | technique | targets | A0003 | Programmable Logic Controller (PLC) | x-mitre-asset--986c455b-0f43-42b6-8360-33ac48bd9990 | asset |  | relationship--f4afb180-4b30-4ed1-b094-3d74d8fd0cf1 | 28 September 2023 | 28 September 2023
T0805 | Block Serial COM | attack-pattern--1c478716-71d9-46a4-9a53-fa5d576adb60 | technique | targets | A0004 | Remote Terminal Unit (RTU) | x-mitre-asset--1769c499-55e5-462f-bab2-c39b8cd5ae32 | asset |  | relationship--ac933d76-8207-4bf7-add2-92b60cf3044b | 28 September 2023 | 28 September 2023
T0805 | Block Serial COM | attack-pattern--1c478716-71d9-46a4-9a53-fa5d576adb60 | technique | targets | A0010 | Safety Controller | x-mitre-asset--69d1b1ef-e918-4cfd-9a98-29debd04cb32 | asset |  | relationship--ed8b97e2-5966-4844-a636-524541a46e43 | 29 September 2023 | 29 September 2023
T0805 | Block Serial COM | attack-pattern--1c478716-71d9-46a4-9a53-fa5d576adb60 | technique | targets | A0011 | Virtual Private Network (VPN) Server | x-mitre-asset--0804f037-a3b9-4715-98e1-9f73d19d6945 | asset |  | relationship--2fe222c4-cc81-473d-956e-235e2961a5c3 | 29 September 2023 | 29 September 2023
T0805 | Block Serial COM | attack-pattern--1c478716-71d9-46a4-9a53-fa5d576adb60 | technique | targets | A0001 | Workstation | x-mitre-asset--f1315d02-9118-4e3b-8cdf-4c2d3f77ce41 | asset |  | relationship--01d002a2-696a-4e22-b227-b0b32f54eaf0 | 29 September 2023 | 29 September 2023
T0806 | Brute Force I/O | attack-pattern--8e7089d3-fba2-44f8-94a8-9a79c53920c4 | technique | targets | A0007 | Control Server | x-mitre-asset--ecb81a8b-022e-4529-a404-55cffca7d3a3 | asset |  | relationship--ccbb44ad-2220-4260-99ce-9142c44fc797 | 28 September 2023 | 28 September 2023
T0806 | Brute Force I/O | attack-pattern--8e7089d3-fba2-44f8-94a8-9a79c53920c4 | technique | targets | A0002 | Human-Machine Interface (HMI) | x-mitre-asset--3a95f7e4-4877-4967-b2e8-e287976c3e64 | asset |  | relationship--c1d77f83-23ec-4128-afd1-ed8ea12281a2 | 29 September 2023 | 29 September 2023
T0806 | Brute Force I/O | attack-pattern--8e7089d3-fba2-44f8-94a8-9a79c53920c4 | technique | targets | A0005 | Intelligent Electronic Device (IED) | x-mitre-asset--75f810ad-b678-4c57-b93b-fdc79bba0c04 | asset |  | relationship--076bfea6-309e-4804-a147-dffe93983481 | 28 September 2023 | 28 September 2023
T0806 | Brute Force I/O | attack-pattern--8e7089d3-fba2-44f8-94a8-9a79c53920c4 | technique | targets | A0003 | Programmable Logic Controller (PLC) | x-mitre-asset--986c455b-0f43-42b6-8360-33ac48bd9990 | asset |  | relationship--ae4e86c6-4bbb-4aba-80fc-c20a8f3d63dc | 28 September 2023 | 28 September 2023
T0806 | Brute Force I/O | attack-pattern--8e7089d3-fba2-44f8-94a8-9a79c53920c4 | technique | targets | A0004 | Remote Terminal Unit (RTU) | x-mitre-asset--1769c499-55e5-462f-bab2-c39b8cd5ae32 | asset |  | relationship--eae674f9-10a2-41e6-9cd3-205af8e69d53 | 28 September 2023 | 28 September 2023
T0806 | Brute Force I/O | attack-pattern--8e7089d3-fba2-44f8-94a8-9a79c53920c4 | technique | targets | A0010 | Safety Controller | x-mitre-asset--69d1b1ef-e918-4cfd-9a98-29debd04cb32 | asset |  | relationship--edaa6f5c-1b59-4ecb-a20f-716a61cdaccb | 29 September 2023 | 29 September 2023
T0892 | Change Credential | attack-pattern--fab8fc7d-f27f-4fbb-9de6-44740aade05f | technique | targets | A0008 | Application Server | x-mitre-asset--973bc51e-c41e-4cec-ac03-9389c71f3d0d | asset |  | relationship--23851bda-49de-4f35-979f-c4e6b5742389 | 09 April 2024 | 09 April 2024
T0892 | Change Credential | attack-pattern--fab8fc7d-f27f-4fbb-9de6-44740aade05f | technique | targets | A0007 | Control Server | x-mitre-asset--ecb81a8b-022e-4529-a404-55cffca7d3a3 | asset |  | relationship--24793eaf-f0d8-4baf-ba3d-900b87cf464d | 09 April 2024 | 09 April 2024
T0892 | Change Credential | attack-pattern--fab8fc7d-f27f-4fbb-9de6-44740aade05f | technique | targets | A0009 | Data Gateway | x-mitre-asset--68388d4f-8138-420b-be2b-5a7dfe9ff6b4 | asset |  | relationship--525d0a51-bbf9-4cda-aec9-562bb05bd3a0 | 09 April 2024 | 09 April 2024
T0892 | Change Credential | attack-pattern--fab8fc7d-f27f-4fbb-9de6-44740aade05f | technique | targets | A0006 | Data Historian | x-mitre-asset--e2c3336a-dd93-44d6-8246-f93cf132c499 | asset |  | relationship--2f7c49a0-89fe-4d18-915c-c321868d47bd | 09 April 2024 | 09 April 2024
T0892 | Change Credential | attack-pattern--fab8fc7d-f27f-4fbb-9de6-44740aade05f | technique | targets | A0002 | Human-Machine Interface (HMI) | x-mitre-asset--3a95f7e4-4877-4967-b2e8-e287976c3e64 | asset |  | relationship--c596f45a-ad65-4673-b316-05378175f35e | 09 April 2024 | 09 April 2024
T0892 | Change Credential | attack-pattern--fab8fc7d-f27f-4fbb-9de6-44740aade05f | technique | targets | A0005 | Intelligent Electronic Device (IED) | x-mitre-asset--75f810ad-b678-4c57-b93b-fdc79bba0c04 | asset |  | relationship--cbc65a60-3b40-4ecf-a10d-8ef1be72568d | 09 April 2024 | 09 April 2024
T0892 | Change Credential | attack-pattern--fab8fc7d-f27f-4fbb-9de6-44740aade05f | technique | targets | A0012 | Jump Host | x-mitre-asset--14932ed5-1098-4cc1-9f57-159ab7366787 | asset |  | relationship--0e191d66-fe38-4f28-ad82-6922bd6bcc81 | 09 April 2024 | 09 April 2024
T0892 | Change Credential | attack-pattern--fab8fc7d-f27f-4fbb-9de6-44740aade05f | technique | targets | A0003 | Programmable Logic Controller (PLC) | x-mitre-asset--986c455b-0f43-42b6-8360-33ac48bd9990 | asset |  | relationship--7dd11d5e-1c1c-4f94-b4bf-4fd59988539b | 09 April 2024 | 09 April 2024
T0892 | Change Credential | attack-pattern--fab8fc7d-f27f-4fbb-9de6-44740aade05f | technique | targets | A0004 | Remote Terminal Unit (RTU) | x-mitre-asset--1769c499-55e5-462f-bab2-c39b8cd5ae32 | asset |  | relationship--6067c069-8e93-4bf0-bb49-97538d55c3de | 09 April 2024 | 09 April 2024
T0892 | Change Credential | attack-pattern--fab8fc7d-f27f-4fbb-9de6-44740aade05f | technique | targets | A0014 | Routers | x-mitre-asset--dcb1d1c1-b195-45bf-b4cf-5b98c5b859a5 | asset |  | relationship--e4c62e59-d14e-4cbc-a4a9-4f64bd523d5a | 09 April 2024 | 09 April 2024
T0892 | Change Credential | attack-pattern--fab8fc7d-f27f-4fbb-9de6-44740aade05f | technique | targets | A0010 | Safety Controller | x-mitre-asset--69d1b1ef-e918-4cfd-9a98-29debd04cb32 | asset |  | relationship--c8222300-6c5e-42d6-ae67-3595407b89fd | 09 April 2024 | 09 April 2024
T0892 | Change Credential | attack-pattern--fab8fc7d-f27f-4fbb-9de6-44740aade05f | technique | targets | A0011 | Virtual Private Network (VPN) Server | x-mitre-asset--0804f037-a3b9-4715-98e1-9f73d19d6945 | asset |  | relationship--16c7240e-0559-4c49-9003-1bfe97074252 | 09 April 2024 | 09 April 2024
T0892 | Change Credential | attack-pattern--fab8fc7d-f27f-4fbb-9de6-44740aade05f | technique | targets | A0001 | Workstation | x-mitre-asset--f1315d02-9118-4e3b-8cdf-4c2d3f77ce41 | asset |  | relationship--c4dd7251-ed87-4629-86b5-090e52a82df2 | 09 April 2024 | 09 April 2024
T0858 | Change Operating Mode | attack-pattern--2883c520-7957-46ca-89bd-dab1ad53b601 | technique | targets | A0003 | Programmable Logic Controller (PLC) | x-mitre-asset--986c455b-0f43-42b6-8360-33ac48bd9990 | asset |  | relationship--e8ef9bb9-1335-4418-b788-f8220dbbe4c8 | 28 September 2023 | 28 September 2023
T0858 | Change Operating Mode | attack-pattern--2883c520-7957-46ca-89bd-dab1ad53b601 | technique | targets | A0010 | Safety Controller | x-mitre-asset--69d1b1ef-e918-4cfd-9a98-29debd04cb32 | asset |  | relationship--e83a79df-2555-4b2f-9ade-b9ed2689ae42 | 29 September 2023 | 29 September 2023
T0807 | Command-Line Interface | attack-pattern--24a9253e-8948-4c98-b751-8e2aee53127c | technique | targets | A0008 | Application Server | x-mitre-asset--973bc51e-c41e-4cec-ac03-9389c71f3d0d | asset |  | relationship--0e263b73-a033-4fac-9d6d-076ab8f8b954 | 29 September 2023 | 29 September 2023
T0807 | Command-Line Interface | attack-pattern--24a9253e-8948-4c98-b751-8e2aee53127c | technique | targets | A0007 | Control Server | x-mitre-asset--ecb81a8b-022e-4529-a404-55cffca7d3a3 | asset |  | relationship--296375b0-817d-4f42-afe1-4308f5edf973 | 28 September 2023 | 28 September 2023
T0807 | Command-Line Interface | attack-pattern--24a9253e-8948-4c98-b751-8e2aee53127c | technique | targets | A0009 | Data Gateway | x-mitre-asset--68388d4f-8138-420b-be2b-5a7dfe9ff6b4 | asset |  | relationship--0a5002d3-cf0d-4e26-9fc4-8faff7f6578a | 29 September 2023 | 29 September 2023
T0807 | Command-Line Interface | attack-pattern--24a9253e-8948-4c98-b751-8e2aee53127c | technique | targets | A0006 | Data Historian | x-mitre-asset--e2c3336a-dd93-44d6-8246-f93cf132c499 | asset |  | relationship--d1a97502-b41d-40a8-aff5-13367fefc642 | 28 September 2023 | 28 September 2023
T0807 | Command-Line Interface | attack-pattern--24a9253e-8948-4c98-b751-8e2aee53127c | technique | targets | A0002 | Human-Machine Interface (HMI) | x-mitre-asset--3a95f7e4-4877-4967-b2e8-e287976c3e64 | asset |  | relationship--033b4401-261f-498b-89f3-2bad9ff5907a | 29 September 2023 | 29 September 2023
T0807 | Command-Line Interface | attack-pattern--24a9253e-8948-4c98-b751-8e2aee53127c | technique | targets | A0012 | Jump Host | x-mitre-asset--14932ed5-1098-4cc1-9f57-159ab7366787 | asset |  | relationship--58a95ec2-0079-4d58-a7ed-02664c1095ba | 28 September 2023 | 28 September 2023
T0807 | Command-Line Interface | attack-pattern--24a9253e-8948-4c98-b751-8e2aee53127c | technique | targets | A0001 | Workstation | x-mitre-asset--f1315d02-9118-4e3b-8cdf-4c2d3f77ce41 | asset |  | relationship--5b14c813-09e2-4709-ab42-94830cf9538c | 29 September 2023 | 29 September 2023
T0885 | Commonly Used Port | attack-pattern--e6c31185-8040-4267-83d3-b217b8a92f07 | technique | targets | A0008 | Application Server | x-mitre-asset--973bc51e-c41e-4cec-ac03-9389c71f3d0d | asset |  | relationship--fac4bc88-af9b-4eec-b041-e4138b49c3c0 | 29 September 2023 | 29 September 2023
T0885 | Commonly Used Port | attack-pattern--e6c31185-8040-4267-83d3-b217b8a92f07 | technique | targets | A0007 | Control Server | x-mitre-asset--ecb81a8b-022e-4529-a404-55cffca7d3a3 | asset |  | relationship--fe22f626-ddf3-4d5e-97d1-058878d7830f | 28 September 2023 | 28 September 2023
T0885 | Commonly Used Port | attack-pattern--e6c31185-8040-4267-83d3-b217b8a92f07 | technique | targets | A0009 | Data Gateway | x-mitre-asset--68388d4f-8138-420b-be2b-5a7dfe9ff6b4 | asset |  | relationship--d5e908f9-eea1-4e55-a406-f24c5dc74b2d | 29 September 2023 | 29 September 2023
T0885 | Commonly Used Port | attack-pattern--e6c31185-8040-4267-83d3-b217b8a92f07 | technique | targets | A0006 | Data Historian | x-mitre-asset--e2c3336a-dd93-44d6-8246-f93cf132c499 | asset |  | relationship--2159458f-87fc-4479-81f4-a2521a378221 | 28 September 2023 | 28 September 2023
T0885 | Commonly Used Port | attack-pattern--e6c31185-8040-4267-83d3-b217b8a92f07 | technique | targets | A0013 | Field I/O | x-mitre-asset--2b676abd-8263-49ea-81a4-78a7e1f776fe | asset |  | relationship--1a3ecee5-0237-4e01-8f02-90092c15a2f0 | 02 October 2023 | 02 October 2023
T0885 | Commonly Used Port | attack-pattern--e6c31185-8040-4267-83d3-b217b8a92f07 | technique | targets | A0002 | Human-Machine Interface (HMI) | x-mitre-asset--3a95f7e4-4877-4967-b2e8-e287976c3e64 | asset |  | relationship--df7b521e-4496-432f-a61d-3094d0c7bc23 | 29 September 2023 | 29 September 2023
T0885 | Commonly Used Port | attack-pattern--e6c31185-8040-4267-83d3-b217b8a92f07 | technique | targets | A0005 | Intelligent Electronic Device (IED) | x-mitre-asset--75f810ad-b678-4c57-b93b-fdc79bba0c04 | asset |  | relationship--5ee01089-2ab6-4cf5-a39d-adf72666eceb | 28 September 2023 | 28 September 2023
T0885 | Commonly Used Port | attack-pattern--e6c31185-8040-4267-83d3-b217b8a92f07 | technique | targets | A0012 | Jump Host | x-mitre-asset--14932ed5-1098-4cc1-9f57-159ab7366787 | asset |  | relationship--d3564f1f-8637-4878-a66a-3e8ea46f7a72 | 28 September 2023 | 28 September 2023
T0885 | Commonly Used Port | attack-pattern--e6c31185-8040-4267-83d3-b217b8a92f07 | technique | targets | A0003 | Programmable Logic Controller (PLC) | x-mitre-asset--986c455b-0f43-42b6-8360-33ac48bd9990 | asset |  | relationship--4a7340fc-0eec-4459-a491-952d736b79ef | 28 September 2023 | 28 September 2023
T0885 | Commonly Used Port | attack-pattern--e6c31185-8040-4267-83d3-b217b8a92f07 | technique | targets | A0004 | Remote Terminal Unit (RTU) | x-mitre-asset--1769c499-55e5-462f-bab2-c39b8cd5ae32 | asset |  | relationship--ee72cc27-2e78-47c4-8786-1351f9bcee97 | 28 September 2023 | 28 September 2023
T0885 | Commonly Used Port | attack-pattern--e6c31185-8040-4267-83d3-b217b8a92f07 | technique | targets | A0014 | Routers | x-mitre-asset--dcb1d1c1-b195-45bf-b4cf-5b98c5b859a5 | asset |  | relationship--106530e1-375a-4ac4-befb-8297b3b05610 | 29 September 2023 | 29 September 2023
T0885 | Commonly Used Port | attack-pattern--e6c31185-8040-4267-83d3-b217b8a92f07 | technique | targets | A0010 | Safety Controller | x-mitre-asset--69d1b1ef-e918-4cfd-9a98-29debd04cb32 | asset |  | relationship--a3f258ea-6d4d-4b0e-8ff2-b91f49dfd4d7 | 29 September 2023 | 29 September 2023
T0885 | Commonly Used Port | attack-pattern--e6c31185-8040-4267-83d3-b217b8a92f07 | technique | targets | A0011 | Virtual Private Network (VPN) Server | x-mitre-asset--0804f037-a3b9-4715-98e1-9f73d19d6945 | asset |  | relationship--413c1c41-6ef9-413b-a75a-e67f1668b3db | 29 September 2023 | 29 September 2023
T0885 | Commonly Used Port | attack-pattern--e6c31185-8040-4267-83d3-b217b8a92f07 | technique | targets | A0001 | Workstation | x-mitre-asset--f1315d02-9118-4e3b-8cdf-4c2d3f77ce41 | asset |  | relationship--b84e1473-f370-42ad-ac3b-7caf3c8cd00e | 29 September 2023 | 29 September 2023
T0884 | Connection Proxy | attack-pattern--d67adac8-e3b9-44f9-9e6d-6c2a7d69dbe4 | technique | targets | A0008 | Application Server | x-mitre-asset--973bc51e-c41e-4cec-ac03-9389c71f3d0d | asset |  | relationship--a1d99bbc-8d7c-4263-a909-95a9507b43c3 | 29 September 2023 | 29 September 2023
T0884 | Connection Proxy | attack-pattern--d67adac8-e3b9-44f9-9e6d-6c2a7d69dbe4 | technique | targets | A0007 | Control Server | x-mitre-asset--ecb81a8b-022e-4529-a404-55cffca7d3a3 | asset |  | relationship--b289c971-3fb7-4c3c-b3d6-cf2702b9384a | 28 September 2023 | 28 September 2023
T0884 | Connection Proxy | attack-pattern--d67adac8-e3b9-44f9-9e6d-6c2a7d69dbe4 | technique | targets | A0009 | Data Gateway | x-mitre-asset--68388d4f-8138-420b-be2b-5a7dfe9ff6b4 | asset |  | relationship--fc189fa0-1235-46ac-a802-f226dc0ec4e1 | 29 September 2023 | 29 September 2023
T0884 | Connection Proxy | attack-pattern--d67adac8-e3b9-44f9-9e6d-6c2a7d69dbe4 | technique | targets | A0006 | Data Historian | x-mitre-asset--e2c3336a-dd93-44d6-8246-f93cf132c499 | asset |  | relationship--bc3a0b1f-f0ec-466f-8cad-8f47b07764c9 | 28 September 2023 | 28 September 2023
T0884 | Connection Proxy | attack-pattern--d67adac8-e3b9-44f9-9e6d-6c2a7d69dbe4 | technique | targets | A0013 | Field I/O | x-mitre-asset--2b676abd-8263-49ea-81a4-78a7e1f776fe | asset |  | relationship--65e25631-05de-4ce2-88cc-52f91cfbdaf2 | 02 October 2023 | 02 October 2023
T0884 | Connection Proxy | attack-pattern--d67adac8-e3b9-44f9-9e6d-6c2a7d69dbe4 | technique | targets | A0002 | Human-Machine Interface (HMI) | x-mitre-asset--3a95f7e4-4877-4967-b2e8-e287976c3e64 | asset |  | relationship--652c1e77-cfea-4452-9762-5ba16f874119 | 29 September 2023 | 29 September 2023
T0884 | Connection Proxy | attack-pattern--d67adac8-e3b9-44f9-9e6d-6c2a7d69dbe4 | technique | targets | A0005 | Intelligent Electronic Device (IED) | x-mitre-asset--75f810ad-b678-4c57-b93b-fdc79bba0c04 | asset |  | relationship--f8456c9b-a4a5-4f13-94e3-54c787b21089 | 28 September 2023 | 28 September 2023
T0884 | Connection Proxy | attack-pattern--d67adac8-e3b9-44f9-9e6d-6c2a7d69dbe4 | technique | targets | A0012 | Jump Host | x-mitre-asset--14932ed5-1098-4cc1-9f57-159ab7366787 | asset |  | relationship--2aaa6840-47fc-455c-9b19-1d27c3afccbe | 28 September 2023 | 28 September 2023
T0884 | Connection Proxy | attack-pattern--d67adac8-e3b9-44f9-9e6d-6c2a7d69dbe4 | technique | targets | A0003 | Programmable Logic Controller (PLC) | x-mitre-asset--986c455b-0f43-42b6-8360-33ac48bd9990 | asset |  | relationship--d48894cb-457e-4a81-82b4-2d735aea5128 | 28 September 2023 | 28 September 2023
T0884 | Connection Proxy | attack-pattern--d67adac8-e3b9-44f9-9e6d-6c2a7d69dbe4 | technique | targets | A0004 | Remote Terminal Unit (RTU) | x-mitre-asset--1769c499-55e5-462f-bab2-c39b8cd5ae32 | asset |  | relationship--07e06d21-e666-4274-838a-ef9996fdc0cd | 28 September 2023 | 28 September 2023
T0884 | Connection Proxy | attack-pattern--d67adac8-e3b9-44f9-9e6d-6c2a7d69dbe4 | technique | targets | A0014 | Routers | x-mitre-asset--dcb1d1c1-b195-45bf-b4cf-5b98c5b859a5 | asset |  | relationship--2289f005-7863-4af5-b681-cdfc03d3f111 | 29 September 2023 | 29 September 2023
T0884 | Connection Proxy | attack-pattern--d67adac8-e3b9-44f9-9e6d-6c2a7d69dbe4 | technique | targets | A0010 | Safety Controller | x-mitre-asset--69d1b1ef-e918-4cfd-9a98-29debd04cb32 | asset |  | relationship--14c73603-a6d2-4a8d-9904-0f8249aaa495 | 29 September 2023 | 29 September 2023
T0884 | Connection Proxy | attack-pattern--d67adac8-e3b9-44f9-9e6d-6c2a7d69dbe4 | technique | targets | A0011 | Virtual Private Network (VPN) Server | x-mitre-asset--0804f037-a3b9-4715-98e1-9f73d19d6945 | asset |  | relationship--f61944a4-fef5-4989-bc3d-68f86e65d7d4 | 29 September 2023 | 29 September 2023
T0884 | Connection Proxy | attack-pattern--d67adac8-e3b9-44f9-9e6d-6c2a7d69dbe4 | technique | targets | A0001 | Workstation | x-mitre-asset--f1315d02-9118-4e3b-8cdf-4c2d3f77ce41 | asset |  | relationship--a93ba793-24dd-47dd-b32c-4c3016124c90 | 29 September 2023 | 29 September 2023
T0809 | Data Destruction | attack-pattern--493832d9-cea6-4b63-abe7-9a65a6473675 | technique | targets | A0008 | Application Server | x-mitre-asset--973bc51e-c41e-4cec-ac03-9389c71f3d0d | asset |  | relationship--38bda770-c470-4358-a9ad-a5b39bec026b | 29 September 2023 | 29 September 2023
T0809 | Data Destruction | attack-pattern--493832d9-cea6-4b63-abe7-9a65a6473675 | technique | targets | A0007 | Control Server | x-mitre-asset--ecb81a8b-022e-4529-a404-55cffca7d3a3 | asset |  | relationship--21aa6331-3419-4049-b180-8349b71e1f2a | 28 September 2023 | 28 September 2023
T0809 | Data Destruction | attack-pattern--493832d9-cea6-4b63-abe7-9a65a6473675 | technique | targets | A0009 | Data Gateway | x-mitre-asset--68388d4f-8138-420b-be2b-5a7dfe9ff6b4 | asset |  | relationship--938ff1d4-acce-4e4e-8a9c-be62799dff8e | 29 September 2023 | 29 September 2023
T0809 | Data Destruction | attack-pattern--493832d9-cea6-4b63-abe7-9a65a6473675 | technique | targets | A0006 | Data Historian | x-mitre-asset--e2c3336a-dd93-44d6-8246-f93cf132c499 | asset |  | relationship--f92764db-a880-4726-9d28-a035170f790c | 28 September 2023 | 28 September 2023
T0809 | Data Destruction | attack-pattern--493832d9-cea6-4b63-abe7-9a65a6473675 | technique | targets | A0013 | Field I/O | x-mitre-asset--2b676abd-8263-49ea-81a4-78a7e1f776fe | asset |  | relationship--ac63d227-ff8a-43b8-81ef-ec4c046c4291 | 02 October 2023 | 02 October 2023
T0809 | Data Destruction | attack-pattern--493832d9-cea6-4b63-abe7-9a65a6473675 | technique | targets | A0002 | Human-Machine Interface (HMI) | x-mitre-asset--3a95f7e4-4877-4967-b2e8-e287976c3e64 | asset |  | relationship--edccbe1f-a07a-405e-9b9a-b247ce3dcc9b | 29 September 2023 | 29 September 2023
T0809 | Data Destruction | attack-pattern--493832d9-cea6-4b63-abe7-9a65a6473675 | technique | targets | A0005 | Intelligent Electronic Device (IED) | x-mitre-asset--75f810ad-b678-4c57-b93b-fdc79bba0c04 | asset |  | relationship--fadbdca3-3c98-497c-a156-e53b89664359 | 28 September 2023 | 28 September 2023
T0809 | Data Destruction | attack-pattern--493832d9-cea6-4b63-abe7-9a65a6473675 | technique | targets | A0012 | Jump Host | x-mitre-asset--14932ed5-1098-4cc1-9f57-159ab7366787 | asset |  | relationship--b21e0340-976d-44b2-94ae-f777199993c6 | 28 September 2023 | 28 September 2023
T0809 | Data Destruction | attack-pattern--493832d9-cea6-4b63-abe7-9a65a6473675 | technique | targets | A0003 | Programmable Logic Controller (PLC) | x-mitre-asset--986c455b-0f43-42b6-8360-33ac48bd9990 | asset |  | relationship--d9fa7d68-a07c-4cf0-bb01-14e2c70c21d5 | 28 September 2023 | 28 September 2023
T0809 | Data Destruction | attack-pattern--493832d9-cea6-4b63-abe7-9a65a6473675 | technique | targets | A0004 | Remote Terminal Unit (RTU) | x-mitre-asset--1769c499-55e5-462f-bab2-c39b8cd5ae32 | asset |  | relationship--16ac0172-02d1-4fda-99c0-61f1cef7dc4b | 28 September 2023 | 28 September 2023
T0809 | Data Destruction | attack-pattern--493832d9-cea6-4b63-abe7-9a65a6473675 | technique | targets | A0014 | Routers | x-mitre-asset--dcb1d1c1-b195-45bf-b4cf-5b98c5b859a5 | asset |  | relationship--18af193c-160a-4cae-9078-4d69de5c2347 | 29 September 2023 | 29 September 2023
T0809 | Data Destruction | attack-pattern--493832d9-cea6-4b63-abe7-9a65a6473675 | technique | targets | A0010 | Safety Controller | x-mitre-asset--69d1b1ef-e918-4cfd-9a98-29debd04cb32 | asset |  | relationship--5201c576-70a5-4b32-8dfd-dd8ac86f096c | 29 September 2023 | 29 September 2023
T0809 | Data Destruction | attack-pattern--493832d9-cea6-4b63-abe7-9a65a6473675 | technique | targets | A0011 | Virtual Private Network (VPN) Server | x-mitre-asset--0804f037-a3b9-4715-98e1-9f73d19d6945 | asset |  | relationship--3dd15958-b159-4d01-b3c2-37bdf9b417b5 | 29 September 2023 | 29 September 2023
T0809 | Data Destruction | attack-pattern--493832d9-cea6-4b63-abe7-9a65a6473675 | technique | targets | A0001 | Workstation | x-mitre-asset--f1315d02-9118-4e3b-8cdf-4c2d3f77ce41 | asset |  | relationship--81806f43-c9aa-486e-8032-4e4665ba0d39 | 29 September 2023 | 29 September 2023
T0811 | Data from Information Repositories | attack-pattern--3405891b-16aa-4bd7-bd7c-733501f9b20f | technique | targets | A0007 | Control Server | x-mitre-asset--ecb81a8b-022e-4529-a404-55cffca7d3a3 | asset |  | relationship--8474e6ef-39c4-4ecc-ba5a-cbd9b32b5c65 | 28 September 2023 | 28 September 2023
T0811 | Data from Information Repositories | attack-pattern--3405891b-16aa-4bd7-bd7c-733501f9b20f | technique | targets | A0006 | Data Historian | x-mitre-asset--e2c3336a-dd93-44d6-8246-f93cf132c499 | asset |  | relationship--0b6cd19f-ee13-4224-9e22-f8a9e626d98f | 28 September 2023 | 28 September 2023
T0893 | Data from Local System | attack-pattern--fa3aa267-da22-4bdd-961f-03223322a8d5 | technique | targets | A0008 | Application Server | x-mitre-asset--973bc51e-c41e-4cec-ac03-9389c71f3d0d | asset |  | relationship--ca225ea0-e813-4205-98db-707b474ae24f | 09 April 2024 | 09 April 2024
T0893 | Data from Local System | attack-pattern--fa3aa267-da22-4bdd-961f-03223322a8d5 | technique | targets | A0007 | Control Server | x-mitre-asset--ecb81a8b-022e-4529-a404-55cffca7d3a3 | asset |  | relationship--484b0873-59ef-41a3-b33d-b3fb41a2c957 | 09 April 2024 | 09 April 2024
T0893 | Data from Local System | attack-pattern--fa3aa267-da22-4bdd-961f-03223322a8d5 | technique | targets | A0006 | Data Historian | x-mitre-asset--e2c3336a-dd93-44d6-8246-f93cf132c499 | asset |  | relationship--66d8f3d7-68e0-48a0-a563-4746922080fc | 09 April 2024 | 09 April 2024
T0893 | Data from Local System | attack-pattern--fa3aa267-da22-4bdd-961f-03223322a8d5 | technique | targets | A0002 | Human-Machine Interface (HMI) | x-mitre-asset--3a95f7e4-4877-4967-b2e8-e287976c3e64 | asset |  | relationship--9537d9c9-ba0d-42d9-b97d-3b28bfe265e6 | 09 April 2024 | 09 April 2024
T0893 | Data from Local System | attack-pattern--fa3aa267-da22-4bdd-961f-03223322a8d5 | technique | targets | A0012 | Jump Host | x-mitre-asset--14932ed5-1098-4cc1-9f57-159ab7366787 | asset |  | relationship--f7d672f6-993b-4036-961d-f6e22e94446c | 09 April 2024 | 09 April 2024
T0893 | Data from Local System | attack-pattern--fa3aa267-da22-4bdd-961f-03223322a8d5 | technique | targets | A0001 | Workstation | x-mitre-asset--f1315d02-9118-4e3b-8cdf-4c2d3f77ce41 | asset |  | relationship--e41a04fe-a142-4294-a9f2-576214e1f985 | 09 April 2024 | 09 April 2024
T0812 | Default Credentials | attack-pattern--8bb4538f-f16f-49f0-a431-70b5444c7349 | technique | targets | A0008 | Application Server | x-mitre-asset--973bc51e-c41e-4cec-ac03-9389c71f3d0d | asset |  | relationship--c2168fe8-be19-4df5-808e-ed87c9c0e1c5 | 29 September 2023 | 29 September 2023
T0812 | Default Credentials | attack-pattern--8bb4538f-f16f-49f0-a431-70b5444c7349 | technique | targets | A0007 | Control Server | x-mitre-asset--ecb81a8b-022e-4529-a404-55cffca7d3a3 | asset |  | relationship--d648b3c7-77d2-42f3-a367-620621b714ab | 28 September 2023 | 28 September 2023
T0812 | Default Credentials | attack-pattern--8bb4538f-f16f-49f0-a431-70b5444c7349 | technique | targets | A0009 | Data Gateway | x-mitre-asset--68388d4f-8138-420b-be2b-5a7dfe9ff6b4 | asset |  | relationship--eac205a6-271b-4a86-acf3-6f4ddefb82c4 | 29 September 2023 | 29 September 2023
T0812 | Default Credentials | attack-pattern--8bb4538f-f16f-49f0-a431-70b5444c7349 | technique | targets | A0006 | Data Historian | x-mitre-asset--e2c3336a-dd93-44d6-8246-f93cf132c499 | asset |  | relationship--f10611e9-4812-4780-a1d5-0ad537dd95fb | 28 September 2023 | 28 September 2023
T0812 | Default Credentials | attack-pattern--8bb4538f-f16f-49f0-a431-70b5444c7349 | technique | targets | A0013 | Field I/O | x-mitre-asset--2b676abd-8263-49ea-81a4-78a7e1f776fe | asset |  | relationship--f19c34b2-ef3a-4581-b604-6639f501e32f | 02 October 2023 | 02 October 2023
T0812 | Default Credentials | attack-pattern--8bb4538f-f16f-49f0-a431-70b5444c7349 | technique | targets | A0002 | Human-Machine Interface (HMI) | x-mitre-asset--3a95f7e4-4877-4967-b2e8-e287976c3e64 | asset |  | relationship--c6a05c20-02d4-42ce-ad5c-280c604e13d8 | 29 September 2023 | 29 September 2023
T0812 | Default Credentials | attack-pattern--8bb4538f-f16f-49f0-a431-70b5444c7349 | technique | targets | A0005 | Intelligent Electronic Device (IED) | x-mitre-asset--75f810ad-b678-4c57-b93b-fdc79bba0c04 | asset |  | relationship--956bbc7f-82c2-4097-8b7b-1e9d732c532d | 28 September 2023 | 28 September 2023
T0812 | Default Credentials | attack-pattern--8bb4538f-f16f-49f0-a431-70b5444c7349 | technique | targets | A0012 | Jump Host | x-mitre-asset--14932ed5-1098-4cc1-9f57-159ab7366787 | asset |  | relationship--688d2041-5c8b-47e0-86e1-a8d16134bdb1 | 28 September 2023 | 28 September 2023
T0812 | Default Credentials | attack-pattern--8bb4538f-f16f-49f0-a431-70b5444c7349 | technique | targets | A0003 | Programmable Logic Controller (PLC) | x-mitre-asset--986c455b-0f43-42b6-8360-33ac48bd9990 | asset |  | relationship--0cab29c6-d196-47b0-8621-10ac3c8a95d8 | 28 September 2023 | 28 September 2023
T0812 | Default Credentials | attack-pattern--8bb4538f-f16f-49f0-a431-70b5444c7349 | technique | targets | A0004 | Remote Terminal Unit (RTU) | x-mitre-asset--1769c499-55e5-462f-bab2-c39b8cd5ae32 | asset |  | relationship--600f0115-94e3-49bf-afa6-0180b3367b94 | 28 September 2023 | 28 September 2023
T0812 | Default Credentials | attack-pattern--8bb4538f-f16f-49f0-a431-70b5444c7349 | technique | targets | A0014 | Routers | x-mitre-asset--dcb1d1c1-b195-45bf-b4cf-5b98c5b859a5 | asset |  | relationship--bf8e68fe-1969-48d1-be0e-ec742378748d | 29 September 2023 | 29 September 2023
T0812 | Default Credentials | attack-pattern--8bb4538f-f16f-49f0-a431-70b5444c7349 | technique | targets | A0010 | Safety Controller | x-mitre-asset--69d1b1ef-e918-4cfd-9a98-29debd04cb32 | asset |  | relationship--aff2fb40-9ef5-42c9-bc7a-4939b509fbf1 | 29 September 2023 | 29 September 2023
T0812 | Default Credentials | attack-pattern--8bb4538f-f16f-49f0-a431-70b5444c7349 | technique | targets | A0011 | Virtual Private Network (VPN) Server | x-mitre-asset--0804f037-a3b9-4715-98e1-9f73d19d6945 | asset |  | relationship--f61e474c-d7be-411e-a30e-0a1ef872fe51 | 29 September 2023 | 29 September 2023
T0812 | Default Credentials | attack-pattern--8bb4538f-f16f-49f0-a431-70b5444c7349 | technique | targets | A0001 | Workstation | x-mitre-asset--f1315d02-9118-4e3b-8cdf-4c2d3f77ce41 | asset |  | relationship--99fa6d92-0c41-44ed-bd30-dd0413785883 | 29 September 2023 | 29 September 2023
T0814 | Denial of Service | attack-pattern--1b22b676-9347-4c55-9a35-ef0dc653db5b | technique | targets | A0007 | Control Server | x-mitre-asset--ecb81a8b-022e-4529-a404-55cffca7d3a3 | asset |  | relationship--eeeb83cb-0a8a-412b-aae2-aede7c43d8e8 | 28 September 2023 | 28 September 2023
T0814 | Denial of Service | attack-pattern--1b22b676-9347-4c55-9a35-ef0dc653db5b | technique | targets | A0009 | Data Gateway | x-mitre-asset--68388d4f-8138-420b-be2b-5a7dfe9ff6b4 | asset |  | relationship--2dc39956-05d1-4dd5-86db-cb70568d73fe | 29 September 2023 | 29 September 2023
T0814 | Denial of Service | attack-pattern--1b22b676-9347-4c55-9a35-ef0dc653db5b | technique | targets | A0006 | Data Historian | x-mitre-asset--e2c3336a-dd93-44d6-8246-f93cf132c499 | asset |  | relationship--4c53b294-973f-4cc2-a781-6c86b8f1c962 | 28 September 2023 | 28 September 2023
T0814 | Denial of Service | attack-pattern--1b22b676-9347-4c55-9a35-ef0dc653db5b | technique | targets | A0013 | Field I/O | x-mitre-asset--2b676abd-8263-49ea-81a4-78a7e1f776fe | asset |  | relationship--39452123-574f-4f3a-95ec-a90170a3d7eb | 02 October 2023 | 02 October 2023
T0814 | Denial of Service | attack-pattern--1b22b676-9347-4c55-9a35-ef0dc653db5b | technique | targets | A0002 | Human-Machine Interface (HMI) | x-mitre-asset--3a95f7e4-4877-4967-b2e8-e287976c3e64 | asset |  | relationship--8530c1ea-fe9f-4b04-be34-7404d5e30e75 | 29 September 2023 | 29 September 2023
T0814 | Denial of Service | attack-pattern--1b22b676-9347-4c55-9a35-ef0dc653db5b | technique | targets | A0005 | Intelligent Electronic Device (IED) | x-mitre-asset--75f810ad-b678-4c57-b93b-fdc79bba0c04 | asset |  | relationship--968fd463-fec4-4b2d-b3c9-950d8471b9a8 | 28 September 2023 | 28 September 2023
T0814 | Denial of Service | attack-pattern--1b22b676-9347-4c55-9a35-ef0dc653db5b | technique | targets | A0012 | Jump Host | x-mitre-asset--14932ed5-1098-4cc1-9f57-159ab7366787 | asset |  | relationship--12fdacea-28f7-4113-ae67-0b19e1ab5e36 | 28 September 2023 | 28 September 2023
T0814 | Denial of Service | attack-pattern--1b22b676-9347-4c55-9a35-ef0dc653db5b | technique | targets | A0003 | Programmable Logic Controller (PLC) | x-mitre-asset--986c455b-0f43-42b6-8360-33ac48bd9990 | asset |  | relationship--b7a9bff5-2e15-4d3d-ac88-84af1239a586 | 28 September 2023 | 28 September 2023
T0814 | Denial of Service | attack-pattern--1b22b676-9347-4c55-9a35-ef0dc653db5b | technique | targets | A0004 | Remote Terminal Unit (RTU) | x-mitre-asset--1769c499-55e5-462f-bab2-c39b8cd5ae32 | asset |  | relationship--ca13a117-aae0-4802-878b-c09f4a04dd31 | 28 September 2023 | 28 September 2023
T0814 | Denial of Service | attack-pattern--1b22b676-9347-4c55-9a35-ef0dc653db5b | technique | targets | A0010 | Safety Controller | x-mitre-asset--69d1b1ef-e918-4cfd-9a98-29debd04cb32 | asset |  | relationship--7bb1dbec-7314-479a-9496-86f8e25041eb | 29 September 2023 | 29 September 2023
T0868 | Detect Operating Mode | attack-pattern--2aa406ed-81c3-4c1d-ba83-cfbee5a2847a | technique | targets | A0003 | Programmable Logic Controller (PLC) | x-mitre-asset--986c455b-0f43-42b6-8360-33ac48bd9990 | asset |  | relationship--2c79920a-f2d1-4114-a1df-924835da645c | 28 September 2023 | 28 September 2023
T0868 | Detect Operating Mode | attack-pattern--2aa406ed-81c3-4c1d-ba83-cfbee5a2847a | technique | targets | A0010 | Safety Controller | x-mitre-asset--69d1b1ef-e918-4cfd-9a98-29debd04cb32 | asset |  | relationship--97e20860-29d9-4738-a9a8-6cc3e4db23f1 | 29 September 2023 | 29 September 2023
T0816 | Device Restart/Shutdown | attack-pattern--25dfc8ad-bd73-4dfd-84a9-3c3d383f76e9 | technique | targets | A0008 | Application Server | x-mitre-asset--973bc51e-c41e-4cec-ac03-9389c71f3d0d | asset |  | relationship--d1bd77d4-9f1a-41ee-bf64-0aa7438e6896 | 29 September 2023 | 29 September 2023
T0816 | Device Restart/Shutdown | attack-pattern--25dfc8ad-bd73-4dfd-84a9-3c3d383f76e9 | technique | targets | A0007 | Control Server | x-mitre-asset--ecb81a8b-022e-4529-a404-55cffca7d3a3 | asset |  | relationship--ede2b798-2f39-419e-a7d3-8f0c733af4c1 | 28 September 2023 | 28 September 2023
T0816 | Device Restart/Shutdown | attack-pattern--25dfc8ad-bd73-4dfd-84a9-3c3d383f76e9 | technique | targets | A0009 | Data Gateway | x-mitre-asset--68388d4f-8138-420b-be2b-5a7dfe9ff6b4 | asset |  | relationship--d455330d-f190-4854-8087-4c2c37003b45 | 29 September 2023 | 29 September 2023
T0816 | Device Restart/Shutdown | attack-pattern--25dfc8ad-bd73-4dfd-84a9-3c3d383f76e9 | technique | targets | A0006 | Data Historian | x-mitre-asset--e2c3336a-dd93-44d6-8246-f93cf132c499 | asset |  | relationship--52bfd00c-2e5b-4e43-bba6-f3b46e241d7b | 28 September 2023 | 28 September 2023
T0816 | Device Restart/Shutdown | attack-pattern--25dfc8ad-bd73-4dfd-84a9-3c3d383f76e9 | technique | targets | A0013 | Field I/O | x-mitre-asset--2b676abd-8263-49ea-81a4-78a7e1f776fe | asset |  | relationship--c58563a8-d757-4476-8ae2-beb2acce38b3 | 02 October 2023 | 02 October 2023
T0816 | Device Restart/Shutdown | attack-pattern--25dfc8ad-bd73-4dfd-84a9-3c3d383f76e9 | technique | targets | A0002 | Human-Machine Interface (HMI) | x-mitre-asset--3a95f7e4-4877-4967-b2e8-e287976c3e64 | asset |  | relationship--02f547fd-2565-4130-a4be-c4ba7b5aeb0c | 29 September 2023 | 29 September 2023
T0816 | Device Restart/Shutdown | attack-pattern--25dfc8ad-bd73-4dfd-84a9-3c3d383f76e9 | technique | targets | A0005 | Intelligent Electronic Device (IED) | x-mitre-asset--75f810ad-b678-4c57-b93b-fdc79bba0c04 | asset |  | relationship--2452cc82-6ee0-4a98-a213-d5e3f3247e07 | 28 September 2023 | 28 September 2023
T0816 | Device Restart/Shutdown | attack-pattern--25dfc8ad-bd73-4dfd-84a9-3c3d383f76e9 | technique | targets | A0012 | Jump Host | x-mitre-asset--14932ed5-1098-4cc1-9f57-159ab7366787 | asset |  | relationship--39f785a8-4175-4d3c-ba64-e20ad4bc2584 | 28 September 2023 | 28 September 2023
T0816 | Device Restart/Shutdown | attack-pattern--25dfc8ad-bd73-4dfd-84a9-3c3d383f76e9 | technique | targets | A0003 | Programmable Logic Controller (PLC) | x-mitre-asset--986c455b-0f43-42b6-8360-33ac48bd9990 | asset |  | relationship--d2985b8a-7a29-4b57-b2f1-cddd79fe4242 | 28 September 2023 | 28 September 2023
T0816 | Device Restart/Shutdown | attack-pattern--25dfc8ad-bd73-4dfd-84a9-3c3d383f76e9 | technique | targets | A0004 | Remote Terminal Unit (RTU) | x-mitre-asset--1769c499-55e5-462f-bab2-c39b8cd5ae32 | asset |  | relationship--7be2d11d-87be-4d1c-8f5b-b7e59ad191ea | 28 September 2023 | 28 September 2023
T0816 | Device Restart/Shutdown | attack-pattern--25dfc8ad-bd73-4dfd-84a9-3c3d383f76e9 | technique | targets | A0014 | Routers | x-mitre-asset--dcb1d1c1-b195-45bf-b4cf-5b98c5b859a5 | asset |  | relationship--3a20ed21-5e69-4a16-a0e3-bace3eba9974 | 29 September 2023 | 29 September 2023
T0816 | Device Restart/Shutdown | attack-pattern--25dfc8ad-bd73-4dfd-84a9-3c3d383f76e9 | technique | targets | A0010 | Safety Controller | x-mitre-asset--69d1b1ef-e918-4cfd-9a98-29debd04cb32 | asset |  | relationship--f531e763-3550-40ba-a6a1-81e208ca12c6 | 29 September 2023 | 29 September 2023
T0816 | Device Restart/Shutdown | attack-pattern--25dfc8ad-bd73-4dfd-84a9-3c3d383f76e9 | technique | targets | A0011 | Virtual Private Network (VPN) Server | x-mitre-asset--0804f037-a3b9-4715-98e1-9f73d19d6945 | asset |  | relationship--1736df4d-188e-4a44-a8b3-6c6cd71dc749 | 29 September 2023 | 29 September 2023
T0816 | Device Restart/Shutdown | attack-pattern--25dfc8ad-bd73-4dfd-84a9-3c3d383f76e9 | technique | targets | A0001 | Workstation | x-mitre-asset--f1315d02-9118-4e3b-8cdf-4c2d3f77ce41 | asset |  | relationship--011f1d16-c9f1-48ac-94f1-165466c155f8 | 29 September 2023 | 29 September 2023
T0817 | Drive-by Compromise | attack-pattern--7830cfcf-b268-4ac0-a69e-73c6affbae9a | technique | targets | A0001 | Workstation | x-mitre-asset--f1315d02-9118-4e3b-8cdf-4c2d3f77ce41 | asset |  | relationship--c5a69738-3e80-421d-aba2-bdab8a4029fd | 29 September 2023 | 29 September 2023
T0871 | Execution through API | attack-pattern--5a2610f6-9fff-41e1-bc27-575ca20383d4 | technique | targets | A0009 | Data Gateway | x-mitre-asset--68388d4f-8138-420b-be2b-5a7dfe9ff6b4 | asset |  | relationship--dbcc492c-782e-4418-8373-dbc7a76498b0 | 29 September 2023 | 29 September 2023
T0871 | Execution through API | attack-pattern--5a2610f6-9fff-41e1-bc27-575ca20383d4 | technique | targets | A0013 | Field I/O | x-mitre-asset--2b676abd-8263-49ea-81a4-78a7e1f776fe | asset |  | relationship--c41d20c8-b99e-4de8-a0e5-3e0ef3b4275b | 02 October 2023 | 02 October 2023
T0871 | Execution through API | attack-pattern--5a2610f6-9fff-41e1-bc27-575ca20383d4 | technique | targets | A0002 | Human-Machine Interface (HMI) | x-mitre-asset--3a95f7e4-4877-4967-b2e8-e287976c3e64 | asset |  | relationship--83a964cb-730c-44e4-859b-b5246159396b | 29 September 2023 | 29 September 2023
T0871 | Execution through API | attack-pattern--5a2610f6-9fff-41e1-bc27-575ca20383d4 | technique | targets | A0005 | Intelligent Electronic Device (IED) | x-mitre-asset--75f810ad-b678-4c57-b93b-fdc79bba0c04 | asset |  | relationship--159fb736-ba92-4564-aa6d-db6f64497763 | 28 September 2023 | 28 September 2023
T0871 | Execution through API | attack-pattern--5a2610f6-9fff-41e1-bc27-575ca20383d4 | technique | targets | A0003 | Programmable Logic Controller (PLC) | x-mitre-asset--986c455b-0f43-42b6-8360-33ac48bd9990 | asset |  | relationship--3b7f39cb-0101-49b0-ab02-a5adb1672688 | 28 September 2023 | 28 September 2023
T0871 | Execution through API | attack-pattern--5a2610f6-9fff-41e1-bc27-575ca20383d4 | technique | targets | A0004 | Remote Terminal Unit (RTU) | x-mitre-asset--1769c499-55e5-462f-bab2-c39b8cd5ae32 | asset |  | relationship--7bd46875-7d59-4d65-8f9b-d48d3cb54a84 | 28 September 2023 | 28 September 2023
T0871 | Execution through API | attack-pattern--5a2610f6-9fff-41e1-bc27-575ca20383d4 | technique | targets | A0010 | Safety Controller | x-mitre-asset--69d1b1ef-e918-4cfd-9a98-29debd04cb32 | asset |  | relationship--3731962f-64e7-4750-ac8b-40b97eef8725 | 29 September 2023 | 29 September 2023
T0871 | Execution through API | attack-pattern--5a2610f6-9fff-41e1-bc27-575ca20383d4 | technique | targets | A0001 | Workstation | x-mitre-asset--f1315d02-9118-4e3b-8cdf-4c2d3f77ce41 | asset |  | relationship--e49e0138-4247-4f3e-a42c-f0dab2f6ffbc | 29 September 2023 | 29 September 2023
T0819 | Exploit Public-Facing Application | attack-pattern--32632a95-6856-47b9-9ab7-fea5cd7dce00 | technique | targets | A0008 | Application Server | x-mitre-asset--973bc51e-c41e-4cec-ac03-9389c71f3d0d | asset |  | relationship--03aab956-54f3-4e4b-93a7-6d1898d91b57 | 29 September 2023 | 29 September 2023
T0819 | Exploit Public-Facing Application | attack-pattern--32632a95-6856-47b9-9ab7-fea5cd7dce00 | technique | targets | A0011 | Virtual Private Network (VPN) Server | x-mitre-asset--0804f037-a3b9-4715-98e1-9f73d19d6945 | asset |  | relationship--8ed7e323-578c-4a62-bf32-0bf2fefa872b | 29 September 2023 | 29 September 2023
T0819 | Exploit Public-Facing Application | attack-pattern--32632a95-6856-47b9-9ab7-fea5cd7dce00 | technique | targets | A0001 | Workstation | x-mitre-asset--f1315d02-9118-4e3b-8cdf-4c2d3f77ce41 | asset |  | relationship--93c336f2-7e7c-4c79-af16-faae03e66121 | 29 September 2023 | 29 September 2023
T0820 | Exploitation for Evasion | attack-pattern--9f947a1c-3860-48a8-8af0-a2dfa3efde03 | technique | targets | A0008 | Application Server | x-mitre-asset--973bc51e-c41e-4cec-ac03-9389c71f3d0d | asset |  | relationship--cf53ff89-3c31-4f8d-83a1-b74dce4c558d | 29 September 2023 | 29 September 2023
T0820 | Exploitation for Evasion | attack-pattern--9f947a1c-3860-48a8-8af0-a2dfa3efde03 | technique | targets | A0007 | Control Server | x-mitre-asset--ecb81a8b-022e-4529-a404-55cffca7d3a3 | asset |  | relationship--9fa6797f-f2cb-4b93-b8eb-f40936e967f3 | 28 September 2023 | 28 September 2023
T0820 | Exploitation for Evasion | attack-pattern--9f947a1c-3860-48a8-8af0-a2dfa3efde03 | technique | targets | A0009 | Data Gateway | x-mitre-asset--68388d4f-8138-420b-be2b-5a7dfe9ff6b4 | asset |  | relationship--3f07067f-0cbc-489c-8722-a33399ebd4f9 | 29 September 2023 | 29 September 2023
T0820 | Exploitation for Evasion | attack-pattern--9f947a1c-3860-48a8-8af0-a2dfa3efde03 | technique | targets | A0006 | Data Historian | x-mitre-asset--e2c3336a-dd93-44d6-8246-f93cf132c499 | asset |  | relationship--6795c92f-848f-488e-9c25-d240f99c9b34 | 28 September 2023 | 28 September 2023
T0820 | Exploitation for Evasion | attack-pattern--9f947a1c-3860-48a8-8af0-a2dfa3efde03 | technique | targets | A0002 | Human-Machine Interface (HMI) | x-mitre-asset--3a95f7e4-4877-4967-b2e8-e287976c3e64 | asset |  | relationship--c27e676e-1ac0-4ec8-bf9d-f540969c6b6f | 29 September 2023 | 29 September 2023
T0820 | Exploitation for Evasion | attack-pattern--9f947a1c-3860-48a8-8af0-a2dfa3efde03 | technique | targets | A0005 | Intelligent Electronic Device (IED) | x-mitre-asset--75f810ad-b678-4c57-b93b-fdc79bba0c04 | asset |  | relationship--32438a90-406c-40f7-a5ac-a1ca92cd51d5 | 28 September 2023 | 28 September 2023
T0820 | Exploitation for Evasion | attack-pattern--9f947a1c-3860-48a8-8af0-a2dfa3efde03 | technique | targets | A0012 | Jump Host | x-mitre-asset--14932ed5-1098-4cc1-9f57-159ab7366787 | asset |  | relationship--399126a9-815d-4c3b-9d5e-f57d698ac742 | 28 September 2023 | 28 September 2023
T0820 | Exploitation for Evasion | attack-pattern--9f947a1c-3860-48a8-8af0-a2dfa3efde03 | technique | targets | A0003 | Programmable Logic Controller (PLC) | x-mitre-asset--986c455b-0f43-42b6-8360-33ac48bd9990 | asset |  | relationship--bbeb2eae-7da2-4477-ad8e-8c67b00c53bc | 28 September 2023 | 28 September 2023
T0820 | Exploitation for Evasion | attack-pattern--9f947a1c-3860-48a8-8af0-a2dfa3efde03 | technique | targets | A0014 | Routers | x-mitre-asset--dcb1d1c1-b195-45bf-b4cf-5b98c5b859a5 | asset |  | relationship--6c31c795-935a-41ad-8db1-d74430f4a553 | 29 September 2023 | 29 September 2023
T0820 | Exploitation for Evasion | attack-pattern--9f947a1c-3860-48a8-8af0-a2dfa3efde03 | technique | targets | A0010 | Safety Controller | x-mitre-asset--69d1b1ef-e918-4cfd-9a98-29debd04cb32 | asset |  | relationship--97f42cef-bc2a-47c5-b408-8e38aab4030e | 29 September 2023 | 29 September 2023
T0820 | Exploitation for Evasion | attack-pattern--9f947a1c-3860-48a8-8af0-a2dfa3efde03 | technique | targets | A0011 | Virtual Private Network (VPN) Server | x-mitre-asset--0804f037-a3b9-4715-98e1-9f73d19d6945 | asset |  | relationship--a6e9bbe1-3e59-45c0-987a-b5354d602dc7 | 29 September 2023 | 29 September 2023
T0820 | Exploitation for Evasion | attack-pattern--9f947a1c-3860-48a8-8af0-a2dfa3efde03 | technique | targets | A0001 | Workstation | x-mitre-asset--f1315d02-9118-4e3b-8cdf-4c2d3f77ce41 | asset |  | relationship--21058f32-3d6e-4381-9288-5c2248e84cce | 29 September 2023 | 29 September 2023
T0890 | Exploitation for Privilege Escalation | attack-pattern--cfe68e93-ce94-4c0f-a57d-3aa72cedd618 | technique | targets | A0008 | Application Server | x-mitre-asset--973bc51e-c41e-4cec-ac03-9389c71f3d0d | asset |  | relationship--910bada1-c923-4009-a9ea-da257072f168 | 29 September 2023 | 29 September 2023
T0890 | Exploitation for Privilege Escalation | attack-pattern--cfe68e93-ce94-4c0f-a57d-3aa72cedd618 | technique | targets | A0007 | Control Server | x-mitre-asset--ecb81a8b-022e-4529-a404-55cffca7d3a3 | asset |  | relationship--1f393d04-36db-4bae-a2a4-53ff12a1240e | 28 September 2023 | 28 September 2023
T0890 | Exploitation for Privilege Escalation | attack-pattern--cfe68e93-ce94-4c0f-a57d-3aa72cedd618 | technique | targets | A0009 | Data Gateway | x-mitre-asset--68388d4f-8138-420b-be2b-5a7dfe9ff6b4 | asset |  | relationship--7b95b2aa-9561-494f-8e02-d36edc14e38b | 29 September 2023 | 29 September 2023
T0890 | Exploitation for Privilege Escalation | attack-pattern--cfe68e93-ce94-4c0f-a57d-3aa72cedd618 | technique | targets | A0006 | Data Historian | x-mitre-asset--e2c3336a-dd93-44d6-8246-f93cf132c499 | asset |  | relationship--f353e8ec-0766-4fbd-86b7-9ea06b52958b | 28 September 2023 | 28 September 2023
T0890 | Exploitation for Privilege Escalation | attack-pattern--cfe68e93-ce94-4c0f-a57d-3aa72cedd618 | technique | targets | A0002 | Human-Machine Interface (HMI) | x-mitre-asset--3a95f7e4-4877-4967-b2e8-e287976c3e64 | asset |  | relationship--798de2f3-218b-4622-a62c-84e3840d45a6 | 29 September 2023 | 29 September 2023
T0890 | Exploitation for Privilege Escalation | attack-pattern--cfe68e93-ce94-4c0f-a57d-3aa72cedd618 | technique | targets | A0005 | Intelligent Electronic Device (IED) | x-mitre-asset--75f810ad-b678-4c57-b93b-fdc79bba0c04 | asset |  | relationship--250212f0-a149-4a14-af83-94f7fcedc021 | 28 September 2023 | 28 September 2023
T0890 | Exploitation for Privilege Escalation | attack-pattern--cfe68e93-ce94-4c0f-a57d-3aa72cedd618 | technique | targets | A0012 | Jump Host | x-mitre-asset--14932ed5-1098-4cc1-9f57-159ab7366787 | asset |  | relationship--2e32e0fd-24cf-4a41-b56d-98ada9f1db8a | 28 September 2023 | 28 September 2023
T0890 | Exploitation for Privilege Escalation | attack-pattern--cfe68e93-ce94-4c0f-a57d-3aa72cedd618 | technique | targets | A0003 | Programmable Logic Controller (PLC) | x-mitre-asset--986c455b-0f43-42b6-8360-33ac48bd9990 | asset |  | relationship--09e9ed5d-bf32-4aee-8441-774e21ffbdb6 | 28 September 2023 | 28 September 2023
T0890 | Exploitation for Privilege Escalation | attack-pattern--cfe68e93-ce94-4c0f-a57d-3aa72cedd618 | technique | targets | A0014 | Routers | x-mitre-asset--dcb1d1c1-b195-45bf-b4cf-5b98c5b859a5 | asset |  | relationship--b774fcb4-43bf-4ff1-98c6-0a94838eacc2 | 29 September 2023 | 29 September 2023
T0890 | Exploitation for Privilege Escalation | attack-pattern--cfe68e93-ce94-4c0f-a57d-3aa72cedd618 | technique | targets | A0010 | Safety Controller | x-mitre-asset--69d1b1ef-e918-4cfd-9a98-29debd04cb32 | asset |  | relationship--1ba485c9-951e-4e07-8e69-1d0efc372f6b | 29 September 2023 | 29 September 2023
T0890 | Exploitation for Privilege Escalation | attack-pattern--cfe68e93-ce94-4c0f-a57d-3aa72cedd618 | technique | targets | A0011 | Virtual Private Network (VPN) Server | x-mitre-asset--0804f037-a3b9-4715-98e1-9f73d19d6945 | asset |  | relationship--5c61c8a2-bfff-43fb-8397-bff864413d74 | 29 September 2023 | 29 September 2023
T0890 | Exploitation for Privilege Escalation | attack-pattern--cfe68e93-ce94-4c0f-a57d-3aa72cedd618 | technique | targets | A0001 | Workstation | x-mitre-asset--f1315d02-9118-4e3b-8cdf-4c2d3f77ce41 | asset |  | relationship--c9fb4adb-8064-426a-838d-c93674fb380b | 29 September 2023 | 29 September 2023
T0866 | Exploitation of Remote Services | attack-pattern--85a45294-08f1-4539-bf00-7da08aa7b0ee | technique | targets | A0008 | Application Server | x-mitre-asset--973bc51e-c41e-4cec-ac03-9389c71f3d0d | asset |  | relationship--c95850f4-4616-435c-b237-f1985833d40e | 29 September 2023 | 29 September 2023
T0866 | Exploitation of Remote Services | attack-pattern--85a45294-08f1-4539-bf00-7da08aa7b0ee | technique | targets | A0007 | Control Server | x-mitre-asset--ecb81a8b-022e-4529-a404-55cffca7d3a3 | asset |  | relationship--adb41ca8-7d2a-4025-b673-db44c9e1f16b | 28 September 2023 | 28 September 2023
T0866 | Exploitation of Remote Services | attack-pattern--85a45294-08f1-4539-bf00-7da08aa7b0ee | technique | targets | A0009 | Data Gateway | x-mitre-asset--68388d4f-8138-420b-be2b-5a7dfe9ff6b4 | asset |  | relationship--a4c64fbc-bac4-44b8-ba52-8fcfa3f674e5 | 29 September 2023 | 29 September 2023
T0866 | Exploitation of Remote Services | attack-pattern--85a45294-08f1-4539-bf00-7da08aa7b0ee | technique | targets | A0006 | Data Historian | x-mitre-asset--e2c3336a-dd93-44d6-8246-f93cf132c499 | asset |  | relationship--88edcf36-a6f2-474f-b9c2-7800b34919a2 | 28 September 2023 | 28 September 2023
T0866 | Exploitation of Remote Services | attack-pattern--85a45294-08f1-4539-bf00-7da08aa7b0ee | technique | targets | A0002 | Human-Machine Interface (HMI) | x-mitre-asset--3a95f7e4-4877-4967-b2e8-e287976c3e64 | asset |  | relationship--1bea0610-432c-4cd7-8e0e-8b7bbd09d738 | 29 September 2023 | 29 September 2023
T0866 | Exploitation of Remote Services | attack-pattern--85a45294-08f1-4539-bf00-7da08aa7b0ee | technique | targets | A0005 | Intelligent Electronic Device (IED) | x-mitre-asset--75f810ad-b678-4c57-b93b-fdc79bba0c04 | asset |  | relationship--456ff399-4925-45d4-aa84-d930eae5348e | 28 September 2023 | 28 September 2023
T0866 | Exploitation of Remote Services | attack-pattern--85a45294-08f1-4539-bf00-7da08aa7b0ee | technique | targets | A0012 | Jump Host | x-mitre-asset--14932ed5-1098-4cc1-9f57-159ab7366787 | asset |  | relationship--a7a2790e-d5ba-4a46-bde3-c698c6ae52ac | 28 September 2023 | 28 September 2023
T0866 | Exploitation of Remote Services | attack-pattern--85a45294-08f1-4539-bf00-7da08aa7b0ee | technique | targets | A0003 | Programmable Logic Controller (PLC) | x-mitre-asset--986c455b-0f43-42b6-8360-33ac48bd9990 | asset |  | relationship--b69905bd-6865-4092-9543-47bd9ae318ec | 28 September 2023 | 28 September 2023
T0866 | Exploitation of Remote Services | attack-pattern--85a45294-08f1-4539-bf00-7da08aa7b0ee | technique | targets | A0004 | Remote Terminal Unit (RTU) | x-mitre-asset--1769c499-55e5-462f-bab2-c39b8cd5ae32 | asset |  | relationship--5a97008b-c23b-4890-ba76-c30cf2a18fba | 28 September 2023 | 28 September 2023
T0866 | Exploitation of Remote Services | attack-pattern--85a45294-08f1-4539-bf00-7da08aa7b0ee | technique | targets | A0014 | Routers | x-mitre-asset--dcb1d1c1-b195-45bf-b4cf-5b98c5b859a5 | asset |  | relationship--4011b9e8-317f-40b9-bd3c-3fb1e99c6542 | 29 September 2023 | 29 September 2023
T0866 | Exploitation of Remote Services | attack-pattern--85a45294-08f1-4539-bf00-7da08aa7b0ee | technique | targets | A0010 | Safety Controller | x-mitre-asset--69d1b1ef-e918-4cfd-9a98-29debd04cb32 | asset |  | relationship--692ff921-c74d-40a4-ab31-879aba5f247a | 29 September 2023 | 29 September 2023
T0866 | Exploitation of Remote Services | attack-pattern--85a45294-08f1-4539-bf00-7da08aa7b0ee | technique | targets | A0011 | Virtual Private Network (VPN) Server | x-mitre-asset--0804f037-a3b9-4715-98e1-9f73d19d6945 | asset |  | relationship--e434db5d-f201-4411-825f-4a50e1e78c75 | 29 September 2023 | 29 September 2023
T0866 | Exploitation of Remote Services | attack-pattern--85a45294-08f1-4539-bf00-7da08aa7b0ee | technique | targets | A0001 | Workstation | x-mitre-asset--f1315d02-9118-4e3b-8cdf-4c2d3f77ce41 | asset |  | relationship--f5c91d82-5f7c-4e40-a85a-4f1909ae5545 | 29 September 2023 | 29 September 2023
T0822 | External Remote Services | attack-pattern--8d2f3bab-507c-4424-b58b-edc977bd215c | technique | targets | A0008 | Application Server | x-mitre-asset--973bc51e-c41e-4cec-ac03-9389c71f3d0d | asset |  | relationship--2f457bef-1721-4e0f-b236-24e4652a31b4 | 29 September 2023 | 29 September 2023
T0822 | External Remote Services | attack-pattern--8d2f3bab-507c-4424-b58b-edc977bd215c | technique | targets | A0009 | Data Gateway | x-mitre-asset--68388d4f-8138-420b-be2b-5a7dfe9ff6b4 | asset |  | relationship--1d6fa472-a1fe-4657-a60d-c7f1c39b1653 | 29 September 2023 | 29 September 2023
T0822 | External Remote Services | attack-pattern--8d2f3bab-507c-4424-b58b-edc977bd215c | technique | targets | A0006 | Data Historian | x-mitre-asset--e2c3336a-dd93-44d6-8246-f93cf132c499 | asset |  | relationship--f13dac1a-090b-40c6-9093-eb4abe0deba8 | 28 September 2023 | 28 September 2023
T0822 | External Remote Services | attack-pattern--8d2f3bab-507c-4424-b58b-edc977bd215c | technique | targets | A0012 | Jump Host | x-mitre-asset--14932ed5-1098-4cc1-9f57-159ab7366787 | asset |  | relationship--ab8bf0a3-0eef-4364-a3f9-f6ab6222afed | 28 September 2023 | 28 September 2023
T0822 | External Remote Services | attack-pattern--8d2f3bab-507c-4424-b58b-edc977bd215c | technique | targets | A0014 | Routers | x-mitre-asset--dcb1d1c1-b195-45bf-b4cf-5b98c5b859a5 | asset |  | relationship--1a96ad0d-84df-4b6b-ba4c-8559de5ec356 | 29 September 2023 | 29 September 2023
T0822 | External Remote Services | attack-pattern--8d2f3bab-507c-4424-b58b-edc977bd215c | technique | targets | A0011 | Virtual Private Network (VPN) Server | x-mitre-asset--0804f037-a3b9-4715-98e1-9f73d19d6945 | asset |  | relationship--75c27f4e-d1e3-490a-9793-a6fc8e326a48 | 29 September 2023 | 29 September 2023
T0823 | Graphical User Interface | attack-pattern--b0628bfc-5376-4a38-9182-f324501cb4cf | technique | targets | A0008 | Application Server | x-mitre-asset--973bc51e-c41e-4cec-ac03-9389c71f3d0d | asset |  | relationship--cc5c77ce-c5a3-4791-b80e-09d35282443a | 29 September 2023 | 29 September 2023
T0823 | Graphical User Interface | attack-pattern--b0628bfc-5376-4a38-9182-f324501cb4cf | technique | targets | A0007 | Control Server | x-mitre-asset--ecb81a8b-022e-4529-a404-55cffca7d3a3 | asset |  | relationship--818ce9d0-8fc2-4a34-a062-f0e6995bdf32 | 28 September 2023 | 28 September 2023
T0823 | Graphical User Interface | attack-pattern--b0628bfc-5376-4a38-9182-f324501cb4cf | technique | targets | A0009 | Data Gateway | x-mitre-asset--68388d4f-8138-420b-be2b-5a7dfe9ff6b4 | asset |  | relationship--03e94c12-cd51-4f39-a33d-c66a31bbf361 | 29 September 2023 | 29 September 2023
T0823 | Graphical User Interface | attack-pattern--b0628bfc-5376-4a38-9182-f324501cb4cf | technique | targets | A0006 | Data Historian | x-mitre-asset--e2c3336a-dd93-44d6-8246-f93cf132c499 | asset |  | relationship--0c72593d-fcc6-4023-8771-bed5e243310e | 28 September 2023 | 28 September 2023
T0823 | Graphical User Interface | attack-pattern--b0628bfc-5376-4a38-9182-f324501cb4cf | technique | targets | A0002 | Human-Machine Interface (HMI) | x-mitre-asset--3a95f7e4-4877-4967-b2e8-e287976c3e64 | asset |  | relationship--1af5c5bb-0d97-4c0a-9174-4dee1ff8b185 | 29 September 2023 | 29 September 2023
T0823 | Graphical User Interface | attack-pattern--b0628bfc-5376-4a38-9182-f324501cb4cf | technique | targets | A0012 | Jump Host | x-mitre-asset--14932ed5-1098-4cc1-9f57-159ab7366787 | asset |  | relationship--4a641966-3cc8-4dd6-aa61-1a96cfff4a05 | 28 September 2023 | 28 September 2023
T0823 | Graphical User Interface | attack-pattern--b0628bfc-5376-4a38-9182-f324501cb4cf | technique | targets | A0001 | Workstation | x-mitre-asset--f1315d02-9118-4e3b-8cdf-4c2d3f77ce41 | asset |  | relationship--740082b7-2411-473a-a59d-4d46cf12f8b5 | 29 September 2023 | 29 September 2023
T0891 | Hardcoded Credentials | attack-pattern--c9a8d958-fcdb-40d2-af4c-461c8031651a | technique | targets | A0013 | Field I/O | x-mitre-asset--2b676abd-8263-49ea-81a4-78a7e1f776fe | asset |  | relationship--8bfeed6a-a0c6-4f11-81b2-f32225c85ac4 | 02 October 2023 | 02 October 2023
T0874 | Hooking | attack-pattern--ab390887-afc0-4715-826d-b1b167d522ae | technique | targets | A0008 | Application Server | x-mitre-asset--973bc51e-c41e-4cec-ac03-9389c71f3d0d | asset |  | relationship--79407d1e-8e16-48c1-939c-ad92f91dd988 | 29 September 2023 | 29 September 2023
T0874 | Hooking | attack-pattern--ab390887-afc0-4715-826d-b1b167d522ae | technique | targets | A0007 | Control Server | x-mitre-asset--ecb81a8b-022e-4529-a404-55cffca7d3a3 | asset |  | relationship--374837a0-6109-4c95-bee6-893b25ac71cf | 28 September 2023 | 28 September 2023
T0874 | Hooking | attack-pattern--ab390887-afc0-4715-826d-b1b167d522ae | technique | targets | A0009 | Data Gateway | x-mitre-asset--68388d4f-8138-420b-be2b-5a7dfe9ff6b4 | asset |  | relationship--25281488-be20-4d83-89d1-1da7ea836037 | 29 September 2023 | 29 September 2023
T0874 | Hooking | attack-pattern--ab390887-afc0-4715-826d-b1b167d522ae | technique | targets | A0006 | Data Historian | x-mitre-asset--e2c3336a-dd93-44d6-8246-f93cf132c499 | asset |  | relationship--4b6a964f-af5c-4ec2-a309-c1ae6b929596 | 28 September 2023 | 28 September 2023
T0874 | Hooking | attack-pattern--ab390887-afc0-4715-826d-b1b167d522ae | technique | targets | A0002 | Human-Machine Interface (HMI) | x-mitre-asset--3a95f7e4-4877-4967-b2e8-e287976c3e64 | asset |  | relationship--21470001-67f2-47cf-af21-784e5024ac1d | 29 September 2023 | 29 September 2023
T0874 | Hooking | attack-pattern--ab390887-afc0-4715-826d-b1b167d522ae | technique | targets | A0005 | Intelligent Electronic Device (IED) | x-mitre-asset--75f810ad-b678-4c57-b93b-fdc79bba0c04 | asset |  | relationship--4d76274d-75bc-4cd0-be6a-3d5d99f73cb7 | 28 September 2023 | 28 September 2023
T0874 | Hooking | attack-pattern--ab390887-afc0-4715-826d-b1b167d522ae | technique | targets | A0012 | Jump Host | x-mitre-asset--14932ed5-1098-4cc1-9f57-159ab7366787 | asset |  | relationship--096c3136-dac9-4729-98c0-c8d870f2bd13 | 28 September 2023 | 28 September 2023
T0874 | Hooking | attack-pattern--ab390887-afc0-4715-826d-b1b167d522ae | technique | targets | A0003 | Programmable Logic Controller (PLC) | x-mitre-asset--986c455b-0f43-42b6-8360-33ac48bd9990 | asset |  | relationship--1fd5badc-0e9f-462c-9738-550e7e8d8ae3 | 28 September 2023 | 28 September 2023
T0874 | Hooking | attack-pattern--ab390887-afc0-4715-826d-b1b167d522ae | technique | targets | A0004 | Remote Terminal Unit (RTU) | x-mitre-asset--1769c499-55e5-462f-bab2-c39b8cd5ae32 | asset |  | relationship--7d42ba22-9595-4463-8dda-c0e47a154fed | 28 September 2023 | 28 September 2023
T0874 | Hooking | attack-pattern--ab390887-afc0-4715-826d-b1b167d522ae | technique | targets | A0014 | Routers | x-mitre-asset--dcb1d1c1-b195-45bf-b4cf-5b98c5b859a5 | asset |  | relationship--9b0b3c25-d87c-452a-a2f9-241234410eb8 | 29 September 2023 | 29 September 2023
T0874 | Hooking | attack-pattern--ab390887-afc0-4715-826d-b1b167d522ae | technique | targets | A0010 | Safety Controller | x-mitre-asset--69d1b1ef-e918-4cfd-9a98-29debd04cb32 | asset |  | relationship--6a476f56-2c07-43be-8054-d978ee8eb924 | 29 September 2023 | 29 September 2023
T0874 | Hooking | attack-pattern--ab390887-afc0-4715-826d-b1b167d522ae | technique | targets | A0011 | Virtual Private Network (VPN) Server | x-mitre-asset--0804f037-a3b9-4715-98e1-9f73d19d6945 | asset |  | relationship--ed3ef546-566a-46c7-918e-7bfa10d05991 | 29 September 2023 | 29 September 2023
T0874 | Hooking | attack-pattern--ab390887-afc0-4715-826d-b1b167d522ae | technique | targets | A0001 | Workstation | x-mitre-asset--f1315d02-9118-4e3b-8cdf-4c2d3f77ce41 | asset |  | relationship--523777f8-4780-4716-807c-08a67450b916 | 29 September 2023 | 29 September 2023
T0877 | I/O Image | attack-pattern--53a48c74-0025-45f4-b04a-baa853df8204 | technique | targets | A0003 | Programmable Logic Controller (PLC) | x-mitre-asset--986c455b-0f43-42b6-8360-33ac48bd9990 | asset |  | relationship--ef60735b-c64b-465c-9e5f-46a4d3a49fb3 | 28 September 2023 | 28 September 2023
T0877 | I/O Image | attack-pattern--53a48c74-0025-45f4-b04a-baa853df8204 | technique | targets | A0010 | Safety Controller | x-mitre-asset--69d1b1ef-e918-4cfd-9a98-29debd04cb32 | asset |  | relationship--46690df4-ddac-4ed4-8987-8706ae68a0cf | 29 September 2023 | 29 September 2023
T0872 | Indicator Removal on Host | attack-pattern--53a26eee-1080-4d17-9762-2027d5a1b805 | technique | targets | A0008 | Application Server | x-mitre-asset--973bc51e-c41e-4cec-ac03-9389c71f3d0d | asset |  | relationship--007a2c53-fc5c-4750-aff0-defb282e178a | 29 September 2023 | 29 September 2023
T0872 | Indicator Removal on Host | attack-pattern--53a26eee-1080-4d17-9762-2027d5a1b805 | technique | targets | A0007 | Control Server | x-mitre-asset--ecb81a8b-022e-4529-a404-55cffca7d3a3 | asset |  | relationship--12d6fc4f-bf06-4146-a387-4cb86f0f44a4 | 28 September 2023 | 28 September 2023
T0872 | Indicator Removal on Host | attack-pattern--53a26eee-1080-4d17-9762-2027d5a1b805 | technique | targets | A0009 | Data Gateway | x-mitre-asset--68388d4f-8138-420b-be2b-5a7dfe9ff6b4 | asset |  | relationship--a466d5b4-39f0-48c1-9a19-f006dc4cb0ac | 29 September 2023 | 29 September 2023
T0872 | Indicator Removal on Host | attack-pattern--53a26eee-1080-4d17-9762-2027d5a1b805 | technique | targets | A0006 | Data Historian | x-mitre-asset--e2c3336a-dd93-44d6-8246-f93cf132c499 | asset |  | relationship--095456bc-898b-4c76-a062-ff0ea90aeab4 | 28 September 2023 | 28 September 2023
T0872 | Indicator Removal on Host | attack-pattern--53a26eee-1080-4d17-9762-2027d5a1b805 | technique | targets | A0002 | Human-Machine Interface (HMI) | x-mitre-asset--3a95f7e4-4877-4967-b2e8-e287976c3e64 | asset |  | relationship--84fd1e14-44a8-4eac-9bfc-67b50ea1acf7 | 29 September 2023 | 29 September 2023
T0872 | Indicator Removal on Host | attack-pattern--53a26eee-1080-4d17-9762-2027d5a1b805 | technique | targets | A0005 | Intelligent Electronic Device (IED) | x-mitre-asset--75f810ad-b678-4c57-b93b-fdc79bba0c04 | asset |  | relationship--577b53a0-44ff-4cc4-b571-455d61e596c0 | 28 September 2023 | 28 September 2023
T0872 | Indicator Removal on Host | attack-pattern--53a26eee-1080-4d17-9762-2027d5a1b805 | technique | targets | A0012 | Jump Host | x-mitre-asset--14932ed5-1098-4cc1-9f57-159ab7366787 | asset |  | relationship--e75f88e6-1ffb-467b-b488-46e91cb3e1e9 | 28 September 2023 | 28 September 2023
T0872 | Indicator Removal on Host | attack-pattern--53a26eee-1080-4d17-9762-2027d5a1b805 | technique | targets | A0003 | Programmable Logic Controller (PLC) | x-mitre-asset--986c455b-0f43-42b6-8360-33ac48bd9990 | asset |  | relationship--897cfc36-4253-4e1e-8825-726dbe9088a2 | 28 September 2023 | 28 September 2023
T0872 | Indicator Removal on Host | attack-pattern--53a26eee-1080-4d17-9762-2027d5a1b805 | technique | targets | A0004 | Remote Terminal Unit (RTU) | x-mitre-asset--1769c499-55e5-462f-bab2-c39b8cd5ae32 | asset |  | relationship--73093c08-ea39-4956-8bff-55e15f6630cd | 28 September 2023 | 28 September 2023
T0872 | Indicator Removal on Host | attack-pattern--53a26eee-1080-4d17-9762-2027d5a1b805 | technique | targets | A0010 | Safety Controller | x-mitre-asset--69d1b1ef-e918-4cfd-9a98-29debd04cb32 | asset |  | relationship--d9de58a6-58fd-499c-ba7d-588239297179 | 29 September 2023 | 29 September 2023
T0872 | Indicator Removal on Host | attack-pattern--53a26eee-1080-4d17-9762-2027d5a1b805 | technique | targets | A0011 | Virtual Private Network (VPN) Server | x-mitre-asset--0804f037-a3b9-4715-98e1-9f73d19d6945 | asset |  | relationship--ed66e087-8877-4146-a16a-44cfd144a3d8 | 29 September 2023 | 29 September 2023
T0872 | Indicator Removal on Host | attack-pattern--53a26eee-1080-4d17-9762-2027d5a1b805 | technique | targets | A0001 | Workstation | x-mitre-asset--f1315d02-9118-4e3b-8cdf-4c2d3f77ce41 | asset |  | relationship--81055366-e78b-40e0-a799-4b536ba03db3 | 29 September 2023 | 29 September 2023
T0883 | Internet Accessible Device | attack-pattern--f8df6b57-14bc-425f-9a91-6f59f6799307 | technique | targets | A0008 | Application Server | x-mitre-asset--973bc51e-c41e-4cec-ac03-9389c71f3d0d | asset |  | relationship--a15d718f-af30-4745-a837-887ba8f48727 | 29 September 2023 | 29 September 2023
T0883 | Internet Accessible Device | attack-pattern--f8df6b57-14bc-425f-9a91-6f59f6799307 | technique | targets | A0011 | Virtual Private Network (VPN) Server | x-mitre-asset--0804f037-a3b9-4715-98e1-9f73d19d6945 | asset |  | relationship--67dae594-4239-4756-a0bc-dee75de19e4c | 29 September 2023 | 29 September 2023
T0883 | Internet Accessible Device | attack-pattern--f8df6b57-14bc-425f-9a91-6f59f6799307 | technique | targets | A0001 | Workstation | x-mitre-asset--f1315d02-9118-4e3b-8cdf-4c2d3f77ce41 | asset |  | relationship--f0d4d23c-2c8c-4731-9b81-7c86fed25b5d | 29 September 2023 | 29 September 2023
T0867 | Lateral Tool Transfer | attack-pattern--ead7bd34-186e-4c79-9a4d-b65bcce6ed9d | technique | targets | A0008 | Application Server | x-mitre-asset--973bc51e-c41e-4cec-ac03-9389c71f3d0d | asset |  | relationship--012fd76f-1a10-4e48-9306-10ffae3f61dd | 29 September 2023 | 29 September 2023
T0867 | Lateral Tool Transfer | attack-pattern--ead7bd34-186e-4c79-9a4d-b65bcce6ed9d | technique | targets | A0007 | Control Server | x-mitre-asset--ecb81a8b-022e-4529-a404-55cffca7d3a3 | asset |  | relationship--372c2e72-d56a-4501-a3bc-31b6b0c8d0be | 28 September 2023 | 28 September 2023
T0867 | Lateral Tool Transfer | attack-pattern--ead7bd34-186e-4c79-9a4d-b65bcce6ed9d | technique | targets | A0013 | Field I/O | x-mitre-asset--2b676abd-8263-49ea-81a4-78a7e1f776fe | asset |  | relationship--45aae58e-1d09-49de-b4c2-837c6f1d5d8f | 02 October 2023 | 02 October 2023
T0867 | Lateral Tool Transfer | attack-pattern--ead7bd34-186e-4c79-9a4d-b65bcce6ed9d | technique | targets | A0012 | Jump Host | x-mitre-asset--14932ed5-1098-4cc1-9f57-159ab7366787 | asset |  | relationship--46798892-d849-43fe-8147-b40cc9da291e | 28 September 2023 | 28 September 2023
T0867 | Lateral Tool Transfer | attack-pattern--ead7bd34-186e-4c79-9a4d-b65bcce6ed9d | technique | targets | A0011 | Virtual Private Network (VPN) Server | x-mitre-asset--0804f037-a3b9-4715-98e1-9f73d19d6945 | asset |  | relationship--11840b30-f0d1-4df5-a960-cdb80749c32a | 29 September 2023 | 29 September 2023
T0867 | Lateral Tool Transfer | attack-pattern--ead7bd34-186e-4c79-9a4d-b65bcce6ed9d | technique | targets | A0001 | Workstation | x-mitre-asset--f1315d02-9118-4e3b-8cdf-4c2d3f77ce41 | asset |  | relationship--d3266f04-3453-492d-b9ea-6fb9d0ce3999 | 29 September 2023 | 29 September 2023
T0835 | Manipulate I/O Image | attack-pattern--36e9f5bc-ac13-4da4-a2f4-01f4877d9004 | technique | targets | A0003 | Programmable Logic Controller (PLC) | x-mitre-asset--986c455b-0f43-42b6-8360-33ac48bd9990 | asset |  | relationship--d96788b4-55dd-48df-bb9b-83b33ca24813 | 28 September 2023 | 28 September 2023
T0835 | Manipulate I/O Image | attack-pattern--36e9f5bc-ac13-4da4-a2f4-01f4877d9004 | technique | targets | A0010 | Safety Controller | x-mitre-asset--69d1b1ef-e918-4cfd-9a98-29debd04cb32 | asset |  | relationship--8a765743-9caf-4c8a-9c58-6fe2c1993108 | 29 September 2023 | 29 September 2023
T0849 | Masquerading | attack-pattern--ba203963-3182-41ac-af14-7e7ebc83cd61 | technique | targets | A0008 | Application Server | x-mitre-asset--973bc51e-c41e-4cec-ac03-9389c71f3d0d | asset |  | relationship--84671396-a556-4a5d-9bb9-cac697277371 | 29 September 2023 | 29 September 2023
T0849 | Masquerading | attack-pattern--ba203963-3182-41ac-af14-7e7ebc83cd61 | technique | targets | A0007 | Control Server | x-mitre-asset--ecb81a8b-022e-4529-a404-55cffca7d3a3 | asset |  | relationship--19e9b914-3cb9-430c-ae02-f8e93fc2d826 | 28 September 2023 | 28 September 2023
T0849 | Masquerading | attack-pattern--ba203963-3182-41ac-af14-7e7ebc83cd61 | technique | targets | A0009 | Data Gateway | x-mitre-asset--68388d4f-8138-420b-be2b-5a7dfe9ff6b4 | asset |  | relationship--b37844c1-0338-44f6-9116-48fa0f079913 | 29 September 2023 | 29 September 2023
T0849 | Masquerading | attack-pattern--ba203963-3182-41ac-af14-7e7ebc83cd61 | technique | targets | A0006 | Data Historian | x-mitre-asset--e2c3336a-dd93-44d6-8246-f93cf132c499 | asset |  | relationship--8d7e2aa5-129a-4060-88ae-9fc066af13c7 | 28 September 2023 | 28 September 2023
T0849 | Masquerading | attack-pattern--ba203963-3182-41ac-af14-7e7ebc83cd61 | technique | targets | A0002 | Human-Machine Interface (HMI) | x-mitre-asset--3a95f7e4-4877-4967-b2e8-e287976c3e64 | asset |  | relationship--78881a3d-59ad-4fbb-8bd2-69388a068584 | 29 September 2023 | 29 September 2023
T0849 | Masquerading | attack-pattern--ba203963-3182-41ac-af14-7e7ebc83cd61 | technique | targets | A0012 | Jump Host | x-mitre-asset--14932ed5-1098-4cc1-9f57-159ab7366787 | asset |  | relationship--e1269074-37f4-460b-8a2a-cd26892d4f8e | 28 September 2023 | 28 September 2023
T0849 | Masquerading | attack-pattern--ba203963-3182-41ac-af14-7e7ebc83cd61 | technique | targets | A0001 | Workstation | x-mitre-asset--f1315d02-9118-4e3b-8cdf-4c2d3f77ce41 | asset |  | relationship--3526acc8-8834-4aaa-87a5-51e587360cf5 | 29 September 2023 | 29 September 2023
T0838 | Modify Alarm Settings | attack-pattern--e5de767e-f513-41cd-aa15-33f6ce5fbf92 | technique | targets | A0009 | Data Gateway | x-mitre-asset--68388d4f-8138-420b-be2b-5a7dfe9ff6b4 | asset |  | relationship--17fd7ffd-63d9-4e1e-8b19-38095b2d65ab | 29 September 2023 | 29 September 2023
T0838 | Modify Alarm Settings | attack-pattern--e5de767e-f513-41cd-aa15-33f6ce5fbf92 | technique | targets | A0002 | Human-Machine Interface (HMI) | x-mitre-asset--3a95f7e4-4877-4967-b2e8-e287976c3e64 | asset |  | relationship--18cdfacf-4eba-4049-b85f-d1cab5106c75 | 29 September 2023 | 29 September 2023
T0838 | Modify Alarm Settings | attack-pattern--e5de767e-f513-41cd-aa15-33f6ce5fbf92 | technique | targets | A0005 | Intelligent Electronic Device (IED) | x-mitre-asset--75f810ad-b678-4c57-b93b-fdc79bba0c04 | asset |  | relationship--58f5c89c-7ed2-4e14-ac07-6e95da16e2f1 | 28 September 2023 | 28 September 2023
T0838 | Modify Alarm Settings | attack-pattern--e5de767e-f513-41cd-aa15-33f6ce5fbf92 | technique | targets | A0003 | Programmable Logic Controller (PLC) | x-mitre-asset--986c455b-0f43-42b6-8360-33ac48bd9990 | asset |  | relationship--71a2c3f5-7383-4bd8-a830-dc2aae62a977 | 28 September 2023 | 28 September 2023
T0838 | Modify Alarm Settings | attack-pattern--e5de767e-f513-41cd-aa15-33f6ce5fbf92 | technique | targets | A0004 | Remote Terminal Unit (RTU) | x-mitre-asset--1769c499-55e5-462f-bab2-c39b8cd5ae32 | asset |  | relationship--e98892d6-e036-4140-adbb-2932dba51a19 | 28 September 2023 | 28 September 2023
T0838 | Modify Alarm Settings | attack-pattern--e5de767e-f513-41cd-aa15-33f6ce5fbf92 | technique | targets | A0010 | Safety Controller | x-mitre-asset--69d1b1ef-e918-4cfd-9a98-29debd04cb32 | asset |  | relationship--da144dd2-c949-4a7f-8c8d-0cb27c52196a | 29 September 2023 | 29 September 2023
T0821 | Modify Controller Tasking | attack-pattern--09a61657-46e1-439e-b3ed-3e4556a78243 | technique | targets | A0003 | Programmable Logic Controller (PLC) | x-mitre-asset--986c455b-0f43-42b6-8360-33ac48bd9990 | asset |  | relationship--f65fa052-5ad0-4fc3-b579-ee33d1225659 | 28 September 2023 | 28 September 2023
T0821 | Modify Controller Tasking | attack-pattern--09a61657-46e1-439e-b3ed-3e4556a78243 | technique | targets | A0010 | Safety Controller | x-mitre-asset--69d1b1ef-e918-4cfd-9a98-29debd04cb32 | asset |  | relationship--63f863e5-7c00-4474-8e43-bbe8bfb05cc3 | 29 September 2023 | 29 September 2023
T0836 | Modify Parameter | attack-pattern--097924ce-a9a9-4039-8591-e0deedfb8722 | technique | targets | A0005 | Intelligent Electronic Device (IED) | x-mitre-asset--75f810ad-b678-4c57-b93b-fdc79bba0c04 | asset |  | relationship--3fe69c6d-6722-44ad-bab7-e34981d68daa | 28 September 2023 | 28 September 2023
T0836 | Modify Parameter | attack-pattern--097924ce-a9a9-4039-8591-e0deedfb8722 | technique | targets | A0003 | Programmable Logic Controller (PLC) | x-mitre-asset--986c455b-0f43-42b6-8360-33ac48bd9990 | asset |  | relationship--cbee31a0-716c-4b10-83f0-aa889bfb4749 | 20 October 2023 | 20 October 2023
T0836 | Modify Parameter | attack-pattern--097924ce-a9a9-4039-8591-e0deedfb8722 | technique | targets | A0004 | Remote Terminal Unit (RTU) | x-mitre-asset--1769c499-55e5-462f-bab2-c39b8cd5ae32 | asset |  | relationship--e915e12c-3d0c-4f60-b119-9414940abb0b | 28 September 2023 | 28 September 2023
T0889 | Modify Program | attack-pattern--fc5fda7e-6b2c-4457-b036-759896a2efa2 | technique | targets | A0003 | Programmable Logic Controller (PLC) | x-mitre-asset--986c455b-0f43-42b6-8360-33ac48bd9990 | asset |  | relationship--ff021e27-63be-41f4-bc4d-2ce75d8a3ecb | 28 September 2023 | 28 September 2023
T0889 | Modify Program | attack-pattern--fc5fda7e-6b2c-4457-b036-759896a2efa2 | technique | targets | A0010 | Safety Controller | x-mitre-asset--69d1b1ef-e918-4cfd-9a98-29debd04cb32 | asset |  | relationship--a1d2df14-6f44-44ac-99c2-3e3f55f53476 | 29 September 2023 | 29 September 2023
T0839 | Module Firmware | attack-pattern--efbf7888-f61b-4572-9c80-7e2965c60707 | technique | targets | A0003 | Programmable Logic Controller (PLC) | x-mitre-asset--986c455b-0f43-42b6-8360-33ac48bd9990 | asset |  | relationship--bffad8de-a807-4216-9753-008a87d9d77f | 28 September 2023 | 28 September 2023
T0839 | Module Firmware | attack-pattern--efbf7888-f61b-4572-9c80-7e2965c60707 | technique | targets | A0010 | Safety Controller | x-mitre-asset--69d1b1ef-e918-4cfd-9a98-29debd04cb32 | asset |  | relationship--5ff26c96-c610-4669-b44e-d6318205be5a | 29 September 2023 | 29 September 2023
T0801 | Monitor Process State | attack-pattern--2d0d40ad-22fa-4cc8-b264-072557e1364b | technique | targets | A0007 | Control Server | x-mitre-asset--ecb81a8b-022e-4529-a404-55cffca7d3a3 | asset |  | relationship--6f950c91-125b-46a0-aa40-239b4de2306a | 28 September 2023 | 28 September 2023
T0801 | Monitor Process State | attack-pattern--2d0d40ad-22fa-4cc8-b264-072557e1364b | technique | targets | A0009 | Data Gateway | x-mitre-asset--68388d4f-8138-420b-be2b-5a7dfe9ff6b4 | asset |  | relationship--e3b04152-0c90-41ff-a333-c5163fa9714f | 29 September 2023 | 29 September 2023
T0801 | Monitor Process State | attack-pattern--2d0d40ad-22fa-4cc8-b264-072557e1364b | technique | targets | A0006 | Data Historian | x-mitre-asset--e2c3336a-dd93-44d6-8246-f93cf132c499 | asset |  | relationship--65d42e15-749b-4f86-86c5-b9f1da1e60c5 | 28 September 2023 | 28 September 2023
T0801 | Monitor Process State | attack-pattern--2d0d40ad-22fa-4cc8-b264-072557e1364b | technique | targets | A0013 | Field I/O | x-mitre-asset--2b676abd-8263-49ea-81a4-78a7e1f776fe | asset |  | relationship--3bc61c8f-3d04-40bd-8239-a15913056bb2 | 02 October 2023 | 02 October 2023
T0801 | Monitor Process State | attack-pattern--2d0d40ad-22fa-4cc8-b264-072557e1364b | technique | targets | A0002 | Human-Machine Interface (HMI) | x-mitre-asset--3a95f7e4-4877-4967-b2e8-e287976c3e64 | asset |  | relationship--4f3a843b-18e7-46e8-8285-9102a2fe62e5 | 29 September 2023 | 29 September 2023
T0801 | Monitor Process State | attack-pattern--2d0d40ad-22fa-4cc8-b264-072557e1364b | technique | targets | A0005 | Intelligent Electronic Device (IED) | x-mitre-asset--75f810ad-b678-4c57-b93b-fdc79bba0c04 | asset |  | relationship--37048032-b41d-47d8-9c73-7b706bef24d1 | 28 September 2023 | 28 September 2023
T0801 | Monitor Process State | attack-pattern--2d0d40ad-22fa-4cc8-b264-072557e1364b | technique | targets | A0003 | Programmable Logic Controller (PLC) | x-mitre-asset--986c455b-0f43-42b6-8360-33ac48bd9990 | asset |  | relationship--99f84b91-32a1-4ade-8de5-5d2a0359302f | 28 September 2023 | 28 September 2023
T0801 | Monitor Process State | attack-pattern--2d0d40ad-22fa-4cc8-b264-072557e1364b | technique | targets | A0004 | Remote Terminal Unit (RTU) | x-mitre-asset--1769c499-55e5-462f-bab2-c39b8cd5ae32 | asset |  | relationship--62abe387-10a2-414b-881c-060b70db2157 | 28 September 2023 | 28 September 2023
T0801 | Monitor Process State | attack-pattern--2d0d40ad-22fa-4cc8-b264-072557e1364b | technique | targets | A0010 | Safety Controller | x-mitre-asset--69d1b1ef-e918-4cfd-9a98-29debd04cb32 | asset |  | relationship--2a451896-81aa-4eed-a444-4d04661adeeb | 29 September 2023 | 29 September 2023
T0834 | Native API | attack-pattern--b52870cc-83f3-473c-b895-72d91751030b | technique | targets | A0008 | Application Server | x-mitre-asset--973bc51e-c41e-4cec-ac03-9389c71f3d0d | asset |  | relationship--6ad3b5cc-7ba1-4287-8c05-d02385f84f72 | 29 September 2023 | 29 September 2023
T0834 | Native API | attack-pattern--b52870cc-83f3-473c-b895-72d91751030b | technique | targets | A0007 | Control Server | x-mitre-asset--ecb81a8b-022e-4529-a404-55cffca7d3a3 | asset |  | relationship--3471632d-253d-469e-9e8c-3b291b4ae88a | 28 September 2023 | 28 September 2023
T0834 | Native API | attack-pattern--b52870cc-83f3-473c-b895-72d91751030b | technique | targets | A0009 | Data Gateway | x-mitre-asset--68388d4f-8138-420b-be2b-5a7dfe9ff6b4 | asset |  | relationship--65aa5a0d-926c-4b04-9509-f66a99639877 | 29 September 2023 | 29 September 2023
T0834 | Native API | attack-pattern--b52870cc-83f3-473c-b895-72d91751030b | technique | targets | A0006 | Data Historian | x-mitre-asset--e2c3336a-dd93-44d6-8246-f93cf132c499 | asset |  | relationship--ecaf20c0-d881-45b4-98f2-a456e07d3643 | 28 September 2023 | 28 September 2023
T0834 | Native API | attack-pattern--b52870cc-83f3-473c-b895-72d91751030b | technique | targets | A0013 | Field I/O | x-mitre-asset--2b676abd-8263-49ea-81a4-78a7e1f776fe | asset |  | relationship--d02812b2-23c3-4dce-bf94-c6e464e86fab | 02 October 2023 | 02 October 2023
T0834 | Native API | attack-pattern--b52870cc-83f3-473c-b895-72d91751030b | technique | targets | A0002 | Human-Machine Interface (HMI) | x-mitre-asset--3a95f7e4-4877-4967-b2e8-e287976c3e64 | asset |  | relationship--6754195a-99cd-4b45-bafd-4a374ae79bbd | 29 September 2023 | 29 September 2023
T0834 | Native API | attack-pattern--b52870cc-83f3-473c-b895-72d91751030b | technique | targets | A0005 | Intelligent Electronic Device (IED) | x-mitre-asset--75f810ad-b678-4c57-b93b-fdc79bba0c04 | asset |  | relationship--7ed1ad67-942a-424e-ad81-8b69a4f0c706 | 28 September 2023 | 28 September 2023
T0834 | Native API | attack-pattern--b52870cc-83f3-473c-b895-72d91751030b | technique | targets | A0012 | Jump Host | x-mitre-asset--14932ed5-1098-4cc1-9f57-159ab7366787 | asset |  | relationship--3ad966be-8cb2-42e6-b696-ef9e3b512e35 | 28 September 2023 | 28 September 2023
T0834 | Native API | attack-pattern--b52870cc-83f3-473c-b895-72d91751030b | technique | targets | A0003 | Programmable Logic Controller (PLC) | x-mitre-asset--986c455b-0f43-42b6-8360-33ac48bd9990 | asset |  | relationship--df321d74-25d6-42da-80e8-3c9a291cb471 | 28 September 2023 | 28 September 2023
T0834 | Native API | attack-pattern--b52870cc-83f3-473c-b895-72d91751030b | technique | targets | A0004 | Remote Terminal Unit (RTU) | x-mitre-asset--1769c499-55e5-462f-bab2-c39b8cd5ae32 | asset |  | relationship--6c9c1c11-c996-4d2b-bbed-d73ae30efd2e | 28 September 2023 | 28 September 2023
T0834 | Native API | attack-pattern--b52870cc-83f3-473c-b895-72d91751030b | technique | targets | A0010 | Safety Controller | x-mitre-asset--69d1b1ef-e918-4cfd-9a98-29debd04cb32 | asset |  | relationship--2346cbf5-b3c8-4110-a66c-6194251d4d49 | 29 September 2023 | 29 September 2023
T0834 | Native API | attack-pattern--b52870cc-83f3-473c-b895-72d91751030b | technique | targets | A0011 | Virtual Private Network (VPN) Server | x-mitre-asset--0804f037-a3b9-4715-98e1-9f73d19d6945 | asset |  | relationship--f1edb034-6dc6-4d6c-8f75-e2cd12213704 | 29 September 2023 | 29 September 2023
T0834 | Native API | attack-pattern--b52870cc-83f3-473c-b895-72d91751030b | technique | targets | A0001 | Workstation | x-mitre-asset--f1315d02-9118-4e3b-8cdf-4c2d3f77ce41 | asset |  | relationship--bd869385-5778-4303-8993-cc6412d12303 | 29 September 2023 | 29 September 2023
T0840 | Network Connection Enumeration | attack-pattern--ea0c980c-5cf0-43a7-a049-59c4c207566e | technique | targets | A0008 | Application Server | x-mitre-asset--973bc51e-c41e-4cec-ac03-9389c71f3d0d | asset |  | relationship--ce3aad7e-1e15-40c7-916b-e25a647e9986 | 29 September 2023 | 29 September 2023
T0840 | Network Connection Enumeration | attack-pattern--ea0c980c-5cf0-43a7-a049-59c4c207566e | technique | targets | A0007 | Control Server | x-mitre-asset--ecb81a8b-022e-4529-a404-55cffca7d3a3 | asset |  | relationship--cb47a3bb-daec-4aa1-9a92-af2a61bb65cd | 28 September 2023 | 28 September 2023
T0840 | Network Connection Enumeration | attack-pattern--ea0c980c-5cf0-43a7-a049-59c4c207566e | technique | targets | A0009 | Data Gateway | x-mitre-asset--68388d4f-8138-420b-be2b-5a7dfe9ff6b4 | asset |  | relationship--6f1479d9-dfd4-4baa-abd5-9847781ef9bf | 29 September 2023 | 29 September 2023
T0840 | Network Connection Enumeration | attack-pattern--ea0c980c-5cf0-43a7-a049-59c4c207566e | technique | targets | A0006 | Data Historian | x-mitre-asset--e2c3336a-dd93-44d6-8246-f93cf132c499 | asset |  | relationship--b7284360-0d80-45bb-8486-263ae8f8fa63 | 28 September 2023 | 28 September 2023
T0840 | Network Connection Enumeration | attack-pattern--ea0c980c-5cf0-43a7-a049-59c4c207566e | technique | targets | A0002 | Human-Machine Interface (HMI) | x-mitre-asset--3a95f7e4-4877-4967-b2e8-e287976c3e64 | asset |  | relationship--503c5256-b611-437e-a4ef-2ee1fd20ab29 | 29 September 2023 | 29 September 2023
T0840 | Network Connection Enumeration | attack-pattern--ea0c980c-5cf0-43a7-a049-59c4c207566e | technique | targets | A0005 | Intelligent Electronic Device (IED) | x-mitre-asset--75f810ad-b678-4c57-b93b-fdc79bba0c04 | asset |  | relationship--a84dd2f5-d4f4-44c1-ba51-4804f40576e1 | 28 September 2023 | 28 September 2023
T0840 | Network Connection Enumeration | attack-pattern--ea0c980c-5cf0-43a7-a049-59c4c207566e | technique | targets | A0012 | Jump Host | x-mitre-asset--14932ed5-1098-4cc1-9f57-159ab7366787 | asset |  | relationship--2fd8a76f-4663-4251-a16d-e1f105a854f9 | 28 September 2023 | 28 September 2023
T0840 | Network Connection Enumeration | attack-pattern--ea0c980c-5cf0-43a7-a049-59c4c207566e | technique | targets | A0003 | Programmable Logic Controller (PLC) | x-mitre-asset--986c455b-0f43-42b6-8360-33ac48bd9990 | asset |  | relationship--b1921480-8499-46a9-8396-2a2d747c5861 | 28 September 2023 | 28 September 2023
T0840 | Network Connection Enumeration | attack-pattern--ea0c980c-5cf0-43a7-a049-59c4c207566e | technique | targets | A0004 | Remote Terminal Unit (RTU) | x-mitre-asset--1769c499-55e5-462f-bab2-c39b8cd5ae32 | asset |  | relationship--e1f28ed0-ec35-4792-ae02-a2d003bd3df4 | 28 September 2023 | 28 September 2023
T0840 | Network Connection Enumeration | attack-pattern--ea0c980c-5cf0-43a7-a049-59c4c207566e | technique | targets | A0010 | Safety Controller | x-mitre-asset--69d1b1ef-e918-4cfd-9a98-29debd04cb32 | asset |  | relationship--a23aefa6-15f5-481c-ac3d-09b8e4b3003b | 29 September 2023 | 29 September 2023
T0840 | Network Connection Enumeration | attack-pattern--ea0c980c-5cf0-43a7-a049-59c4c207566e | technique | targets | A0011 | Virtual Private Network (VPN) Server | x-mitre-asset--0804f037-a3b9-4715-98e1-9f73d19d6945 | asset |  | relationship--24d17e8f-0c0f-41d1-aa83-8b69b8d30be5 | 29 September 2023 | 29 September 2023
T0840 | Network Connection Enumeration | attack-pattern--ea0c980c-5cf0-43a7-a049-59c4c207566e | technique | targets | A0001 | Workstation | x-mitre-asset--f1315d02-9118-4e3b-8cdf-4c2d3f77ce41 | asset |  | relationship--1cf89a8b-c0f6-4ffb-ae39-36e2a9d3b081 | 29 September 2023 | 29 September 2023
T0842 | Network Sniffing | attack-pattern--38213338-1aab-479d-949b-c81b66ccca5c | technique | targets | A0008 | Application Server | x-mitre-asset--973bc51e-c41e-4cec-ac03-9389c71f3d0d | asset |  | relationship--37aeaf27-6bbe-4949-ba77-37649e38f8b2 | 29 September 2023 | 29 September 2023
T0842 | Network Sniffing | attack-pattern--38213338-1aab-479d-949b-c81b66ccca5c | technique | targets | A0007 | Control Server | x-mitre-asset--ecb81a8b-022e-4529-a404-55cffca7d3a3 | asset |  | relationship--0d52eea3-394e-492b-944b-9ccb6348329d | 28 September 2023 | 28 September 2023
T0842 | Network Sniffing | attack-pattern--38213338-1aab-479d-949b-c81b66ccca5c | technique | targets | A0009 | Data Gateway | x-mitre-asset--68388d4f-8138-420b-be2b-5a7dfe9ff6b4 | asset |  | relationship--52e828db-58d0-443e-8d94-54d265d9606e | 29 September 2023 | 29 September 2023
T0842 | Network Sniffing | attack-pattern--38213338-1aab-479d-949b-c81b66ccca5c | technique | targets | A0006 | Data Historian | x-mitre-asset--e2c3336a-dd93-44d6-8246-f93cf132c499 | asset |  | relationship--3d3c5d24-be5c-42e8-98ca-3b04382df39a | 28 September 2023 | 28 September 2023
T0842 | Network Sniffing | attack-pattern--38213338-1aab-479d-949b-c81b66ccca5c | technique | targets | A0002 | Human-Machine Interface (HMI) | x-mitre-asset--3a95f7e4-4877-4967-b2e8-e287976c3e64 | asset |  | relationship--9951eb11-8140-420d-8e2d-56fbe0ff0134 | 29 September 2023 | 29 September 2023
T0842 | Network Sniffing | attack-pattern--38213338-1aab-479d-949b-c81b66ccca5c | technique | targets | A0005 | Intelligent Electronic Device (IED) | x-mitre-asset--75f810ad-b678-4c57-b93b-fdc79bba0c04 | asset |  | relationship--32d15d1a-04ba-4035-907a-e2871425e8d1 | 28 September 2023 | 28 September 2023
T0842 | Network Sniffing | attack-pattern--38213338-1aab-479d-949b-c81b66ccca5c | technique | targets | A0012 | Jump Host | x-mitre-asset--14932ed5-1098-4cc1-9f57-159ab7366787 | asset |  | relationship--d5b532fe-3df9-4f92-a0f0-9c92823cdb6a | 28 September 2023 | 28 September 2023
T0842 | Network Sniffing | attack-pattern--38213338-1aab-479d-949b-c81b66ccca5c | technique | targets | A0003 | Programmable Logic Controller (PLC) | x-mitre-asset--986c455b-0f43-42b6-8360-33ac48bd9990 | asset |  | relationship--86a8d6aa-beff-4343-a0b2-dd099202b2dc | 28 September 2023 | 28 September 2023
T0842 | Network Sniffing | attack-pattern--38213338-1aab-479d-949b-c81b66ccca5c | technique | targets | A0004 | Remote Terminal Unit (RTU) | x-mitre-asset--1769c499-55e5-462f-bab2-c39b8cd5ae32 | asset |  | relationship--1a9ca148-a456-4b66-805f-a2bdfc7a947d | 28 September 2023 | 28 September 2023
T0842 | Network Sniffing | attack-pattern--38213338-1aab-479d-949b-c81b66ccca5c | technique | targets | A0010 | Safety Controller | x-mitre-asset--69d1b1ef-e918-4cfd-9a98-29debd04cb32 | asset |  | relationship--3dd35c9a-146d-4370-80ac-69fed35d81a1 | 29 September 2023 | 29 September 2023
T0842 | Network Sniffing | attack-pattern--38213338-1aab-479d-949b-c81b66ccca5c | technique | targets | A0011 | Virtual Private Network (VPN) Server | x-mitre-asset--0804f037-a3b9-4715-98e1-9f73d19d6945 | asset |  | relationship--c233df49-e450-4151-8a0f-1765faf3d75a | 29 September 2023 | 29 September 2023
T0842 | Network Sniffing | attack-pattern--38213338-1aab-479d-949b-c81b66ccca5c | technique | targets | A0001 | Workstation | x-mitre-asset--f1315d02-9118-4e3b-8cdf-4c2d3f77ce41 | asset |  | relationship--0ba1db3a-389a-4937-975b-d2dc0142cb4b | 29 September 2023 | 29 September 2023
T0861 | Point & Tag Identification | attack-pattern--25852363-5968-4673-b81d-341d5ed90bd1 | technique | targets | A0007 | Control Server | x-mitre-asset--ecb81a8b-022e-4529-a404-55cffca7d3a3 | asset |  | relationship--d89d9778-4695-4c97-bf6d-1d0fbabb41fa | 28 September 2023 | 28 September 2023
T0861 | Point & Tag Identification | attack-pattern--25852363-5968-4673-b81d-341d5ed90bd1 | technique | targets | A0009 | Data Gateway | x-mitre-asset--68388d4f-8138-420b-be2b-5a7dfe9ff6b4 | asset |  | relationship--b2e8914a-91bc-42df-8b64-22e5365ede6f | 29 September 2023 | 29 September 2023
T0861 | Point & Tag Identification | attack-pattern--25852363-5968-4673-b81d-341d5ed90bd1 | technique | targets | A0006 | Data Historian | x-mitre-asset--e2c3336a-dd93-44d6-8246-f93cf132c499 | asset |  | relationship--f5621ad9-c905-42e3-b59b-e0ae7b9051c7 | 28 September 2023 | 28 September 2023
T0861 | Point & Tag Identification | attack-pattern--25852363-5968-4673-b81d-341d5ed90bd1 | technique | targets | A0002 | Human-Machine Interface (HMI) | x-mitre-asset--3a95f7e4-4877-4967-b2e8-e287976c3e64 | asset |  | relationship--dfb20521-91c2-4f55-b92a-dab959759b78 | 29 September 2023 | 29 September 2023
T0861 | Point & Tag Identification | attack-pattern--25852363-5968-4673-b81d-341d5ed90bd1 | technique | targets | A0005 | Intelligent Electronic Device (IED) | x-mitre-asset--75f810ad-b678-4c57-b93b-fdc79bba0c04 | asset |  | relationship--eadb4ca5-ee99-4169-a926-95b1ff82e960 | 28 September 2023 | 28 September 2023
T0861 | Point & Tag Identification | attack-pattern--25852363-5968-4673-b81d-341d5ed90bd1 | technique | targets | A0003 | Programmable Logic Controller (PLC) | x-mitre-asset--986c455b-0f43-42b6-8360-33ac48bd9990 | asset |  | relationship--fdc20415-c9a1-405e-80af-3d297894e8fa | 28 September 2023 | 28 September 2023
T0861 | Point & Tag Identification | attack-pattern--25852363-5968-4673-b81d-341d5ed90bd1 | technique | targets | A0004 | Remote Terminal Unit (RTU) | x-mitre-asset--1769c499-55e5-462f-bab2-c39b8cd5ae32 | asset |  | relationship--6c470aa0-b119-4078-80fc-2b66a4d6eac4 | 28 September 2023 | 28 September 2023
T0861 | Point & Tag Identification | attack-pattern--25852363-5968-4673-b81d-341d5ed90bd1 | technique | targets | A0010 | Safety Controller | x-mitre-asset--69d1b1ef-e918-4cfd-9a98-29debd04cb32 | asset |  | relationship--c37f097a-9698-412f-9e96-4d350bcd2790 | 29 September 2023 | 29 September 2023
T0843 | Program Download | attack-pattern--be69c571-d746-4b1f-bdd0-c0c9817e9068 | technique | targets | A0003 | Programmable Logic Controller (PLC) | x-mitre-asset--986c455b-0f43-42b6-8360-33ac48bd9990 | asset |  | relationship--41dbf626-b968-4b51-9f7d-aaea14d39b4d | 28 September 2023 | 28 September 2023
T0843 | Program Download | attack-pattern--be69c571-d746-4b1f-bdd0-c0c9817e9068 | technique | targets | A0010 | Safety Controller | x-mitre-asset--69d1b1ef-e918-4cfd-9a98-29debd04cb32 | asset |  | relationship--af802091-fee7-4d15-a845-fb4ee3c26d6d | 29 September 2023 | 29 September 2023
T0845 | Program Upload | attack-pattern--3067b85e-271e-4bc5-81ad-ab1a81d411e3 | technique | targets | A0003 | Programmable Logic Controller (PLC) | x-mitre-asset--986c455b-0f43-42b6-8360-33ac48bd9990 | asset |  | relationship--432b2dc0-52ff-488f-a5e9-c1e510fc7a0b | 28 September 2023 | 28 September 2023
T0845 | Program Upload | attack-pattern--3067b85e-271e-4bc5-81ad-ab1a81d411e3 | technique | targets | A0010 | Safety Controller | x-mitre-asset--69d1b1ef-e918-4cfd-9a98-29debd04cb32 | asset |  | relationship--524ffb0f-40ae-4c97-a098-d14001fffa31 | 29 September 2023 | 29 September 2023
T0873 | Project File Infection | attack-pattern--e72425f8-9ae6-41d3-bfdb-e1b865e60722 | technique | targets | A0001 | Workstation | x-mitre-asset--f1315d02-9118-4e3b-8cdf-4c2d3f77ce41 | asset |  | relationship--29c2757d-c5f6-4c8d-bbdd-3629cb14dd81 | 29 September 2023 | 29 September 2023
T0886 | Remote Services | attack-pattern--e1f9cdd2-9511-4fca-90d7-f3e92cfdd0bf | technique | targets | A0008 | Application Server | x-mitre-asset--973bc51e-c41e-4cec-ac03-9389c71f3d0d | asset |  | relationship--67ae8423-c401-4c11-93d3-0454c288d934 | 29 September 2023 | 29 September 2023
T0886 | Remote Services | attack-pattern--e1f9cdd2-9511-4fca-90d7-f3e92cfdd0bf | technique | targets | A0007 | Control Server | x-mitre-asset--ecb81a8b-022e-4529-a404-55cffca7d3a3 | asset |  | relationship--3aa2691d-d88d-4467-ae3e-242b3bac22ea | 28 September 2023 | 28 September 2023
T0886 | Remote Services | attack-pattern--e1f9cdd2-9511-4fca-90d7-f3e92cfdd0bf | technique | targets | A0009 | Data Gateway | x-mitre-asset--68388d4f-8138-420b-be2b-5a7dfe9ff6b4 | asset |  | relationship--f05a2592-00f9-4f1f-ba55-395af5444b96 | 29 September 2023 | 29 September 2023
T0886 | Remote Services | attack-pattern--e1f9cdd2-9511-4fca-90d7-f3e92cfdd0bf | technique | targets | A0006 | Data Historian | x-mitre-asset--e2c3336a-dd93-44d6-8246-f93cf132c499 | asset |  | relationship--def57041-6bb4-453a-bf04-188b9e97a35d | 28 September 2023 | 28 September 2023
T0886 | Remote Services | attack-pattern--e1f9cdd2-9511-4fca-90d7-f3e92cfdd0bf | technique | targets | A0002 | Human-Machine Interface (HMI) | x-mitre-asset--3a95f7e4-4877-4967-b2e8-e287976c3e64 | asset |  | relationship--a287bc05-20cb-4476-ba1f-15bfde6e601d | 29 September 2023 | 29 September 2023
T0886 | Remote Services | attack-pattern--e1f9cdd2-9511-4fca-90d7-f3e92cfdd0bf | technique | targets | A0012 | Jump Host | x-mitre-asset--14932ed5-1098-4cc1-9f57-159ab7366787 | asset |  | relationship--eb171086-88e1-4f24-bd7e-c3f8b3c3283b | 28 September 2023 | 28 September 2023
T0886 | Remote Services | attack-pattern--e1f9cdd2-9511-4fca-90d7-f3e92cfdd0bf | technique | targets | A0011 | Virtual Private Network (VPN) Server | x-mitre-asset--0804f037-a3b9-4715-98e1-9f73d19d6945 | asset |  | relationship--d611b750-95e5-4f73-8f16-38db0a34a2e0 | 29 September 2023 | 29 September 2023
T0846 | Remote System Discovery | attack-pattern--d5a69cfb-fc2a-46cb-99eb-74b236db5061 | technique | targets | A0008 | Application Server | x-mitre-asset--973bc51e-c41e-4cec-ac03-9389c71f3d0d | asset |  | relationship--84fa50ff-bb84-4ab6-b759-658c57532c42 | 29 September 2023 | 29 September 2023
T0846 | Remote System Discovery | attack-pattern--d5a69cfb-fc2a-46cb-99eb-74b236db5061 | technique | targets | A0007 | Control Server | x-mitre-asset--ecb81a8b-022e-4529-a404-55cffca7d3a3 | asset |  | relationship--232c7049-7609-46a9-8bbe-38672713f853 | 28 September 2023 | 28 September 2023
T0846 | Remote System Discovery | attack-pattern--d5a69cfb-fc2a-46cb-99eb-74b236db5061 | technique | targets | A0009 | Data Gateway | x-mitre-asset--68388d4f-8138-420b-be2b-5a7dfe9ff6b4 | asset |  | relationship--026ba3e5-ae3b-4a8b-83c0-ea8327cd9e50 | 29 September 2023 | 29 September 2023
T0846 | Remote System Discovery | attack-pattern--d5a69cfb-fc2a-46cb-99eb-74b236db5061 | technique | targets | A0006 | Data Historian | x-mitre-asset--e2c3336a-dd93-44d6-8246-f93cf132c499 | asset |  | relationship--28e89bca-04a2-462f-9d84-d5dc4d55d98e | 28 September 2023 | 28 September 2023
T0846 | Remote System Discovery | attack-pattern--d5a69cfb-fc2a-46cb-99eb-74b236db5061 | technique | targets | A0002 | Human-Machine Interface (HMI) | x-mitre-asset--3a95f7e4-4877-4967-b2e8-e287976c3e64 | asset |  | relationship--d8f95008-33c9-4572-9916-023d8de449b1 | 29 September 2023 | 29 September 2023
T0846 | Remote System Discovery | attack-pattern--d5a69cfb-fc2a-46cb-99eb-74b236db5061 | technique | targets | A0005 | Intelligent Electronic Device (IED) | x-mitre-asset--75f810ad-b678-4c57-b93b-fdc79bba0c04 | asset |  | relationship--04aad4a8-8b8c-45d9-bb34-508fe4792863 | 28 September 2023 | 28 September 2023
T0846 | Remote System Discovery | attack-pattern--d5a69cfb-fc2a-46cb-99eb-74b236db5061 | technique | targets | A0012 | Jump Host | x-mitre-asset--14932ed5-1098-4cc1-9f57-159ab7366787 | asset |  | relationship--dac96d76-b9b8-4278-9f5b-62f4992e2ac8 | 28 September 2023 | 28 September 2023
T0846 | Remote System Discovery | attack-pattern--d5a69cfb-fc2a-46cb-99eb-74b236db5061 | technique | targets | A0003 | Programmable Logic Controller (PLC) | x-mitre-asset--986c455b-0f43-42b6-8360-33ac48bd9990 | asset |  | relationship--0b2d0517-9943-413e-a6f9-30c6d5ce8c42 | 28 September 2023 | 28 September 2023
T0846 | Remote System Discovery | attack-pattern--d5a69cfb-fc2a-46cb-99eb-74b236db5061 | technique | targets | A0004 | Remote Terminal Unit (RTU) | x-mitre-asset--1769c499-55e5-462f-bab2-c39b8cd5ae32 | asset |  | relationship--4f7cc4b9-fe3a-4883-97cc-4d2a44c55be9 | 28 September 2023 | 28 September 2023
T0846 | Remote System Discovery | attack-pattern--d5a69cfb-fc2a-46cb-99eb-74b236db5061 | technique | targets | A0010 | Safety Controller | x-mitre-asset--69d1b1ef-e918-4cfd-9a98-29debd04cb32 | asset |  | relationship--bb3938a6-85ec-4f34-8bcd-6051de7e9259 | 29 September 2023 | 29 September 2023
T0846 | Remote System Discovery | attack-pattern--d5a69cfb-fc2a-46cb-99eb-74b236db5061 | technique | targets | A0011 | Virtual Private Network (VPN) Server | x-mitre-asset--0804f037-a3b9-4715-98e1-9f73d19d6945 | asset |  | relationship--53d7a78d-1431-49e8-944c-62c875e58a20 | 29 September 2023 | 29 September 2023
T0846 | Remote System Discovery | attack-pattern--d5a69cfb-fc2a-46cb-99eb-74b236db5061 | technique | targets | A0001 | Workstation | x-mitre-asset--f1315d02-9118-4e3b-8cdf-4c2d3f77ce41 | asset |  | relationship--2b7d57d7-3802-4b59-99c6-1e1597fe78d1 | 29 September 2023 | 29 September 2023
T0888 | Remote System Information Discovery | attack-pattern--2fedbe69-581f-447d-8a78-32ee7db939a9 | technique | targets | A0008 | Application Server | x-mitre-asset--973bc51e-c41e-4cec-ac03-9389c71f3d0d | asset |  | relationship--79c6d710-baf4-411e-a3f5-9cb8d42b7c19 | 29 September 2023 | 29 September 2023
T0888 | Remote System Information Discovery | attack-pattern--2fedbe69-581f-447d-8a78-32ee7db939a9 | technique | targets | A0007 | Control Server | x-mitre-asset--ecb81a8b-022e-4529-a404-55cffca7d3a3 | asset |  | relationship--cfaead3c-3db5-400f-bd15-dfbc57cf0185 | 28 September 2023 | 28 September 2023
T0888 | Remote System Information Discovery | attack-pattern--2fedbe69-581f-447d-8a78-32ee7db939a9 | technique | targets | A0009 | Data Gateway | x-mitre-asset--68388d4f-8138-420b-be2b-5a7dfe9ff6b4 | asset |  | relationship--aa7a0f45-e027-4d79-8413-5d807f44c1ba | 29 September 2023 | 29 September 2023
T0888 | Remote System Information Discovery | attack-pattern--2fedbe69-581f-447d-8a78-32ee7db939a9 | technique | targets | A0006 | Data Historian | x-mitre-asset--e2c3336a-dd93-44d6-8246-f93cf132c499 | asset |  | relationship--fe265dd7-2c1a-4c75-8aa8-12d0c82c7926 | 28 September 2023 | 28 September 2023
T0888 | Remote System Information Discovery | attack-pattern--2fedbe69-581f-447d-8a78-32ee7db939a9 | technique | targets | A0013 | Field I/O | x-mitre-asset--2b676abd-8263-49ea-81a4-78a7e1f776fe | asset |  | relationship--d3d4f469-9847-41ef-a478-5eaf6003d483 | 02 October 2023 | 02 October 2023
T0888 | Remote System Information Discovery | attack-pattern--2fedbe69-581f-447d-8a78-32ee7db939a9 | technique | targets | A0002 | Human-Machine Interface (HMI) | x-mitre-asset--3a95f7e4-4877-4967-b2e8-e287976c3e64 | asset |  | relationship--56896f6b-27fe-4396-bfea-d3c1a7580b18 | 29 September 2023 | 29 September 2023
T0888 | Remote System Information Discovery | attack-pattern--2fedbe69-581f-447d-8a78-32ee7db939a9 | technique | targets | A0005 | Intelligent Electronic Device (IED) | x-mitre-asset--75f810ad-b678-4c57-b93b-fdc79bba0c04 | asset |  | relationship--368558ce-e8a6-4375-b54f-47c2ab31e38d | 28 September 2023 | 28 September 2023
T0888 | Remote System Information Discovery | attack-pattern--2fedbe69-581f-447d-8a78-32ee7db939a9 | technique | targets | A0012 | Jump Host | x-mitre-asset--14932ed5-1098-4cc1-9f57-159ab7366787 | asset |  | relationship--3a76a181-8706-4bc4-9c66-7e809fec44ca | 28 September 2023 | 28 September 2023
T0888 | Remote System Information Discovery | attack-pattern--2fedbe69-581f-447d-8a78-32ee7db939a9 | technique | targets | A0003 | Programmable Logic Controller (PLC) | x-mitre-asset--986c455b-0f43-42b6-8360-33ac48bd9990 | asset |  | relationship--4c1df272-9c2a-4647-8d05-3c0de1613e12 | 28 September 2023 | 28 September 2023
T0888 | Remote System Information Discovery | attack-pattern--2fedbe69-581f-447d-8a78-32ee7db939a9 | technique | targets | A0004 | Remote Terminal Unit (RTU) | x-mitre-asset--1769c499-55e5-462f-bab2-c39b8cd5ae32 | asset |  | relationship--24e1f6cf-44c3-4a3f-9839-5cd6398cc0fe | 28 September 2023 | 28 September 2023
T0888 | Remote System Information Discovery | attack-pattern--2fedbe69-581f-447d-8a78-32ee7db939a9 | technique | targets | A0010 | Safety Controller | x-mitre-asset--69d1b1ef-e918-4cfd-9a98-29debd04cb32 | asset |  | relationship--e79825fb-3bd0-41e7-9bdd-257cd3ab44a2 | 29 September 2023 | 29 September 2023
T0888 | Remote System Information Discovery | attack-pattern--2fedbe69-581f-447d-8a78-32ee7db939a9 | technique | targets | A0011 | Virtual Private Network (VPN) Server | x-mitre-asset--0804f037-a3b9-4715-98e1-9f73d19d6945 | asset |  | relationship--e17c3b74-69d8-47b2-88d4-adcaf418ab74 | 29 September 2023 | 29 September 2023
T0888 | Remote System Information Discovery | attack-pattern--2fedbe69-581f-447d-8a78-32ee7db939a9 | technique | targets | A0001 | Workstation | x-mitre-asset--f1315d02-9118-4e3b-8cdf-4c2d3f77ce41 | asset |  | relationship--b6309476-8268-4c47-920b-8a556cd8ae4c | 29 September 2023 | 29 September 2023
T0847 | Replication Through Removable Media | attack-pattern--c267bbee-bb59-47fe-85e0-3ed210337c21 | technique | targets | A0008 | Application Server | x-mitre-asset--973bc51e-c41e-4cec-ac03-9389c71f3d0d | asset |  | relationship--a2f0b9ba-2d6e-43a5-adca-3ec42dba5ce9 | 29 September 2023 | 29 September 2023
T0847 | Replication Through Removable Media | attack-pattern--c267bbee-bb59-47fe-85e0-3ed210337c21 | technique | targets | A0007 | Control Server | x-mitre-asset--ecb81a8b-022e-4529-a404-55cffca7d3a3 | asset |  | relationship--ed3ce006-cf41-46f6-bd86-054314c130dc | 28 September 2023 | 28 September 2023
T0847 | Replication Through Removable Media | attack-pattern--c267bbee-bb59-47fe-85e0-3ed210337c21 | technique | targets | A0009 | Data Gateway | x-mitre-asset--68388d4f-8138-420b-be2b-5a7dfe9ff6b4 | asset |  | relationship--cf8a816c-30ee-4147-a48f-d797fb145a04 | 29 September 2023 | 29 September 2023
T0847 | Replication Through Removable Media | attack-pattern--c267bbee-bb59-47fe-85e0-3ed210337c21 | technique | targets | A0006 | Data Historian | x-mitre-asset--e2c3336a-dd93-44d6-8246-f93cf132c499 | asset |  | relationship--6f72c60e-2739-40b6-b6a9-66d2a3d1833e | 28 September 2023 | 28 September 2023
T0847 | Replication Through Removable Media | attack-pattern--c267bbee-bb59-47fe-85e0-3ed210337c21 | technique | targets | A0013 | Field I/O | x-mitre-asset--2b676abd-8263-49ea-81a4-78a7e1f776fe | asset |  | relationship--0b2a6fc5-3416-4d78-96cb-f6325c91ab91 | 02 October 2023 | 02 October 2023
T0847 | Replication Through Removable Media | attack-pattern--c267bbee-bb59-47fe-85e0-3ed210337c21 | technique | targets | A0002 | Human-Machine Interface (HMI) | x-mitre-asset--3a95f7e4-4877-4967-b2e8-e287976c3e64 | asset |  | relationship--287b247f-8ec3-4d8d-a521-050ac8c791ad | 29 September 2023 | 29 September 2023
T0847 | Replication Through Removable Media | attack-pattern--c267bbee-bb59-47fe-85e0-3ed210337c21 | technique | targets | A0005 | Intelligent Electronic Device (IED) | x-mitre-asset--75f810ad-b678-4c57-b93b-fdc79bba0c04 | asset |  | relationship--d7b07d40-fbdb-41e9-b610-57de10fa41e5 | 28 September 2023 | 28 September 2023
T0847 | Replication Through Removable Media | attack-pattern--c267bbee-bb59-47fe-85e0-3ed210337c21 | technique | targets | A0012 | Jump Host | x-mitre-asset--14932ed5-1098-4cc1-9f57-159ab7366787 | asset |  | relationship--2138f4ee-5111-4469-92bb-1fc82a6822b4 | 28 September 2023 | 28 September 2023
T0847 | Replication Through Removable Media | attack-pattern--c267bbee-bb59-47fe-85e0-3ed210337c21 | technique | targets | A0003 | Programmable Logic Controller (PLC) | x-mitre-asset--986c455b-0f43-42b6-8360-33ac48bd9990 | asset |  | relationship--9c23121e-14bb-4382-b54d-2ea02a2815b5 | 28 September 2023 | 28 September 2023
T0847 | Replication Through Removable Media | attack-pattern--c267bbee-bb59-47fe-85e0-3ed210337c21 | technique | targets | A0004 | Remote Terminal Unit (RTU) | x-mitre-asset--1769c499-55e5-462f-bab2-c39b8cd5ae32 | asset |  | relationship--32bcf2cf-3311-4ef1-9bf4-4bfe14832b3b | 28 September 2023 | 28 September 2023
T0847 | Replication Through Removable Media | attack-pattern--c267bbee-bb59-47fe-85e0-3ed210337c21 | technique | targets | A0010 | Safety Controller | x-mitre-asset--69d1b1ef-e918-4cfd-9a98-29debd04cb32 | asset |  | relationship--e4bc29f2-87c8-491d-b51b-d6cede7c1972 | 29 September 2023 | 29 September 2023
T0847 | Replication Through Removable Media | attack-pattern--c267bbee-bb59-47fe-85e0-3ed210337c21 | technique | targets | A0011 | Virtual Private Network (VPN) Server | x-mitre-asset--0804f037-a3b9-4715-98e1-9f73d19d6945 | asset |  | relationship--d58d8b19-90bc-4a7f-840d-076be296ff20 | 29 September 2023 | 29 September 2023
T0847 | Replication Through Removable Media | attack-pattern--c267bbee-bb59-47fe-85e0-3ed210337c21 | technique | targets | A0001 | Workstation | x-mitre-asset--f1315d02-9118-4e3b-8cdf-4c2d3f77ce41 | asset |  | relationship--43344cd7-5004-4dac-8b62-8899105fa265 | 29 September 2023 | 29 September 2023
T0848 | Rogue Master | attack-pattern--b14395bd-5419-4ef4-9bd8-696936f509bb | technique | targets | A0007 | Control Server | x-mitre-asset--ecb81a8b-022e-4529-a404-55cffca7d3a3 | asset |  | relationship--a221bbb3-5f4f-4879-ae1d-37e8d3022039 | 28 September 2023 | 28 September 2023
T0848 | Rogue Master | attack-pattern--b14395bd-5419-4ef4-9bd8-696936f509bb | technique | targets | A0009 | Data Gateway | x-mitre-asset--68388d4f-8138-420b-be2b-5a7dfe9ff6b4 | asset |  | relationship--7efa1a31-da21-4925-aab0-96a012d5b2a7 | 29 September 2023 | 29 September 2023
T0848 | Rogue Master | attack-pattern--b14395bd-5419-4ef4-9bd8-696936f509bb | technique | targets | A0006 | Data Historian | x-mitre-asset--e2c3336a-dd93-44d6-8246-f93cf132c499 | asset |  | relationship--c65e39eb-f6d1-4e3a-9070-b2fa7ea35b36 | 28 September 2023 | 28 September 2023
T0848 | Rogue Master | attack-pattern--b14395bd-5419-4ef4-9bd8-696936f509bb | technique | targets | A0002 | Human-Machine Interface (HMI) | x-mitre-asset--3a95f7e4-4877-4967-b2e8-e287976c3e64 | asset |  | relationship--4059da6f-b52b-4265-8bf9-3ad6154dbde4 | 29 September 2023 | 29 September 2023
T0848 | Rogue Master | attack-pattern--b14395bd-5419-4ef4-9bd8-696936f509bb | technique | targets | A0005 | Intelligent Electronic Device (IED) | x-mitre-asset--75f810ad-b678-4c57-b93b-fdc79bba0c04 | asset |  | relationship--75e6adae-06a7-47e9-878e-74ca73004c3b | 28 September 2023 | 28 September 2023
T0848 | Rogue Master | attack-pattern--b14395bd-5419-4ef4-9bd8-696936f509bb | technique | targets | A0003 | Programmable Logic Controller (PLC) | x-mitre-asset--986c455b-0f43-42b6-8360-33ac48bd9990 | asset |  | relationship--4981a944-b3ad-4d78-9881-a17d458e3422 | 28 September 2023 | 28 September 2023
T0848 | Rogue Master | attack-pattern--b14395bd-5419-4ef4-9bd8-696936f509bb | technique | targets | A0004 | Remote Terminal Unit (RTU) | x-mitre-asset--1769c499-55e5-462f-bab2-c39b8cd5ae32 | asset |  | relationship--0bc90405-24a9-4f84-a1bb-bf953dbca016 | 28 September 2023 | 28 September 2023
T0848 | Rogue Master | attack-pattern--b14395bd-5419-4ef4-9bd8-696936f509bb | technique | targets | A0010 | Safety Controller | x-mitre-asset--69d1b1ef-e918-4cfd-9a98-29debd04cb32 | asset |  | relationship--f7215c1f-7bd7-41bd-8466-76caac225c7c | 29 September 2023 | 29 September 2023
T0851 | Rootkit | attack-pattern--3b6b9246-43f8-4c69-ad7a-2b11cfe0a0d9 | technique | targets | A0008 | Application Server | x-mitre-asset--973bc51e-c41e-4cec-ac03-9389c71f3d0d | asset |  | relationship--144f6ce7-d2b2-4a76-85d2-251191a0d2cc | 29 September 2023 | 29 September 2023
T0851 | Rootkit | attack-pattern--3b6b9246-43f8-4c69-ad7a-2b11cfe0a0d9 | technique | targets | A0007 | Control Server | x-mitre-asset--ecb81a8b-022e-4529-a404-55cffca7d3a3 | asset |  | relationship--77f3a64d-227d-487f-8484-89007e05b59f | 28 September 2023 | 28 September 2023
T0851 | Rootkit | attack-pattern--3b6b9246-43f8-4c69-ad7a-2b11cfe0a0d9 | technique | targets | A0009 | Data Gateway | x-mitre-asset--68388d4f-8138-420b-be2b-5a7dfe9ff6b4 | asset |  | relationship--66d041e2-d9e8-46cc-88ee-8e5c1cec8702 | 29 September 2023 | 29 September 2023
T0851 | Rootkit | attack-pattern--3b6b9246-43f8-4c69-ad7a-2b11cfe0a0d9 | technique | targets | A0006 | Data Historian | x-mitre-asset--e2c3336a-dd93-44d6-8246-f93cf132c499 | asset |  | relationship--d23fd724-563d-4f49-8bcd-09c653728cd3 | 28 September 2023 | 28 September 2023
T0851 | Rootkit | attack-pattern--3b6b9246-43f8-4c69-ad7a-2b11cfe0a0d9 | technique | targets | A0013 | Field I/O | x-mitre-asset--2b676abd-8263-49ea-81a4-78a7e1f776fe | asset |  | relationship--be0f7d83-2441-4259-b411-46e0d10566b1 | 02 October 2023 | 02 October 2023
T0851 | Rootkit | attack-pattern--3b6b9246-43f8-4c69-ad7a-2b11cfe0a0d9 | technique | targets | A0002 | Human-Machine Interface (HMI) | x-mitre-asset--3a95f7e4-4877-4967-b2e8-e287976c3e64 | asset |  | relationship--b33f2abc-a218-425b-9a90-b75445b7e142 | 29 September 2023 | 29 September 2023
T0851 | Rootkit | attack-pattern--3b6b9246-43f8-4c69-ad7a-2b11cfe0a0d9 | technique | targets | A0005 | Intelligent Electronic Device (IED) | x-mitre-asset--75f810ad-b678-4c57-b93b-fdc79bba0c04 | asset |  | relationship--09e0c991-1707-431b-a0fd-fd8215e6d552 | 28 September 2023 | 28 September 2023
T0851 | Rootkit | attack-pattern--3b6b9246-43f8-4c69-ad7a-2b11cfe0a0d9 | technique | targets | A0012 | Jump Host | x-mitre-asset--14932ed5-1098-4cc1-9f57-159ab7366787 | asset |  | relationship--758773e3-d23d-44db-b5d3-643cde5b41f1 | 28 September 2023 | 28 September 2023
T0851 | Rootkit | attack-pattern--3b6b9246-43f8-4c69-ad7a-2b11cfe0a0d9 | technique | targets | A0003 | Programmable Logic Controller (PLC) | x-mitre-asset--986c455b-0f43-42b6-8360-33ac48bd9990 | asset |  | relationship--77566f94-5e26-41c9-892f-2f62b395afe7 | 28 September 2023 | 28 September 2023
T0851 | Rootkit | attack-pattern--3b6b9246-43f8-4c69-ad7a-2b11cfe0a0d9 | technique | targets | A0010 | Safety Controller | x-mitre-asset--69d1b1ef-e918-4cfd-9a98-29debd04cb32 | asset |  | relationship--49242ea8-4813-49f7-8bd4-9668216cceeb | 29 September 2023 | 29 September 2023
T0851 | Rootkit | attack-pattern--3b6b9246-43f8-4c69-ad7a-2b11cfe0a0d9 | technique | targets | A0011 | Virtual Private Network (VPN) Server | x-mitre-asset--0804f037-a3b9-4715-98e1-9f73d19d6945 | asset |  | relationship--0f5710a7-f015-40b8-ad3d-f281699f2b72 | 29 September 2023 | 29 September 2023
T0851 | Rootkit | attack-pattern--3b6b9246-43f8-4c69-ad7a-2b11cfe0a0d9 | technique | targets | A0001 | Workstation | x-mitre-asset--f1315d02-9118-4e3b-8cdf-4c2d3f77ce41 | asset |  | relationship--bf9f227c-e306-4257-add1-39c7c2e42040 | 29 September 2023 | 29 September 2023
T0852 | Screen Capture | attack-pattern--c5e3cdbc-0387-4be9-8f83-ff5c0865f377 | technique | targets | A0002 | Human-Machine Interface (HMI) | x-mitre-asset--3a95f7e4-4877-4967-b2e8-e287976c3e64 | asset |  | relationship--bf8f90a2-4d3a-436d-87d0-eff060fb2302 | 29 September 2023 | 29 September 2023
T0852 | Screen Capture | attack-pattern--c5e3cdbc-0387-4be9-8f83-ff5c0865f377 | technique | targets | A0012 | Jump Host | x-mitre-asset--14932ed5-1098-4cc1-9f57-159ab7366787 | asset |  | relationship--e95fe824-4df1-49a2-abf7-5d76fb47ef42 | 28 September 2023 | 28 September 2023
T0852 | Screen Capture | attack-pattern--c5e3cdbc-0387-4be9-8f83-ff5c0865f377 | technique | targets | A0001 | Workstation | x-mitre-asset--f1315d02-9118-4e3b-8cdf-4c2d3f77ce41 | asset |  | relationship--f72a7a30-bab4-445b-b226-d5c3cd1a5846 | 29 September 2023 | 29 September 2023
T0853 | Scripting | attack-pattern--2dc2b567-8821-49f9-9045-8740f3d0b958 | technique | targets | A0008 | Application Server | x-mitre-asset--973bc51e-c41e-4cec-ac03-9389c71f3d0d | asset |  | relationship--7ebee5d3-ce7f-436c-8b4a-087363d6b858 | 29 September 2023 | 29 September 2023
T0853 | Scripting | attack-pattern--2dc2b567-8821-49f9-9045-8740f3d0b958 | technique | targets | A0007 | Control Server | x-mitre-asset--ecb81a8b-022e-4529-a404-55cffca7d3a3 | asset |  | relationship--bd7509cc-a7e5-4e29-b615-225dfbdd3c4a | 28 September 2023 | 28 September 2023
T0853 | Scripting | attack-pattern--2dc2b567-8821-49f9-9045-8740f3d0b958 | technique | targets | A0009 | Data Gateway | x-mitre-asset--68388d4f-8138-420b-be2b-5a7dfe9ff6b4 | asset |  | relationship--1b94c927-0445-4ed8-80f1-7b31418f60b5 | 29 September 2023 | 29 September 2023
T0853 | Scripting | attack-pattern--2dc2b567-8821-49f9-9045-8740f3d0b958 | technique | targets | A0006 | Data Historian | x-mitre-asset--e2c3336a-dd93-44d6-8246-f93cf132c499 | asset |  | relationship--4d7eecfc-4dd6-470c-a604-4c8239ac2be4 | 28 September 2023 | 28 September 2023
T0853 | Scripting | attack-pattern--2dc2b567-8821-49f9-9045-8740f3d0b958 | technique | targets | A0002 | Human-Machine Interface (HMI) | x-mitre-asset--3a95f7e4-4877-4967-b2e8-e287976c3e64 | asset |  | relationship--db46e84f-435e-4022-b484-e6d2e253660c | 29 September 2023 | 29 September 2023
T0853 | Scripting | attack-pattern--2dc2b567-8821-49f9-9045-8740f3d0b958 | technique | targets | A0012 | Jump Host | x-mitre-asset--14932ed5-1098-4cc1-9f57-159ab7366787 | asset |  | relationship--3334e647-fd5d-481d-a7f9-66f73911a57a | 28 September 2023 | 28 September 2023
T0853 | Scripting | attack-pattern--2dc2b567-8821-49f9-9045-8740f3d0b958 | technique | targets | A0001 | Workstation | x-mitre-asset--f1315d02-9118-4e3b-8cdf-4c2d3f77ce41 | asset |  | relationship--97f863d7-e68a-4cc8-ab3b-a7e9a1cc2319 | 29 September 2023 | 29 September 2023
T0881 | Service Stop | attack-pattern--063b5b92-5361-481a-9c3f-95492ed9a2d8 | technique | targets | A0008 | Application Server | x-mitre-asset--973bc51e-c41e-4cec-ac03-9389c71f3d0d | asset |  | relationship--2d0bed1d-342b-44a0-aec8-e6d7c6596fa2 | 29 September 2023 | 29 September 2023
T0881 | Service Stop | attack-pattern--063b5b92-5361-481a-9c3f-95492ed9a2d8 | technique | targets | A0007 | Control Server | x-mitre-asset--ecb81a8b-022e-4529-a404-55cffca7d3a3 | asset |  | relationship--7584e57f-1258-4c47-b18d-99019a586e6c | 28 September 2023 | 28 September 2023
T0881 | Service Stop | attack-pattern--063b5b92-5361-481a-9c3f-95492ed9a2d8 | technique | targets | A0009 | Data Gateway | x-mitre-asset--68388d4f-8138-420b-be2b-5a7dfe9ff6b4 | asset |  | relationship--ed095993-bc85-431e-9621-437143f16d44 | 29 September 2023 | 29 September 2023
T0881 | Service Stop | attack-pattern--063b5b92-5361-481a-9c3f-95492ed9a2d8 | technique | targets | A0006 | Data Historian | x-mitre-asset--e2c3336a-dd93-44d6-8246-f93cf132c499 | asset |  | relationship--5968cbde-b3da-46df-a8bd-a30c2d85363b | 28 September 2023 | 28 September 2023
T0881 | Service Stop | attack-pattern--063b5b92-5361-481a-9c3f-95492ed9a2d8 | technique | targets | A0002 | Human-Machine Interface (HMI) | x-mitre-asset--3a95f7e4-4877-4967-b2e8-e287976c3e64 | asset |  | relationship--4768c731-3be9-44b8-a217-dfbececa57d9 | 29 September 2023 | 29 September 2023
T0881 | Service Stop | attack-pattern--063b5b92-5361-481a-9c3f-95492ed9a2d8 | technique | targets | A0005 | Intelligent Electronic Device (IED) | x-mitre-asset--75f810ad-b678-4c57-b93b-fdc79bba0c04 | asset |  | relationship--2f9c25af-d2e2-4793-85bf-6e2696384a50 | 28 September 2023 | 28 September 2023
T0881 | Service Stop | attack-pattern--063b5b92-5361-481a-9c3f-95492ed9a2d8 | technique | targets | A0012 | Jump Host | x-mitre-asset--14932ed5-1098-4cc1-9f57-159ab7366787 | asset |  | relationship--7b814e39-71fc-4e99-b46f-b24eca6cc780 | 28 September 2023 | 28 September 2023
T0881 | Service Stop | attack-pattern--063b5b92-5361-481a-9c3f-95492ed9a2d8 | technique | targets | A0004 | Remote Terminal Unit (RTU) | x-mitre-asset--1769c499-55e5-462f-bab2-c39b8cd5ae32 | asset |  | relationship--54a7bc3f-c05f-4fb3-a980-ffc8750a0a56 | 28 September 2023 | 28 September 2023
T0881 | Service Stop | attack-pattern--063b5b92-5361-481a-9c3f-95492ed9a2d8 | technique | targets | A0010 | Safety Controller | x-mitre-asset--69d1b1ef-e918-4cfd-9a98-29debd04cb32 | asset |  | relationship--d80f9deb-ba2a-4a07-aa23-81c423cf4a18 | 29 September 2023 | 29 September 2023
T0881 | Service Stop | attack-pattern--063b5b92-5361-481a-9c3f-95492ed9a2d8 | technique | targets | A0011 | Virtual Private Network (VPN) Server | x-mitre-asset--0804f037-a3b9-4715-98e1-9f73d19d6945 | asset |  | relationship--59b53303-e4df-49ec-8e5a-812f2b4265a8 | 29 September 2023 | 29 September 2023
T0881 | Service Stop | attack-pattern--063b5b92-5361-481a-9c3f-95492ed9a2d8 | technique | targets | A0001 | Workstation | x-mitre-asset--f1315d02-9118-4e3b-8cdf-4c2d3f77ce41 | asset |  | relationship--605f3853-b007-4134-8a2d-6a81a35e7676 | 29 September 2023 | 29 September 2023
T0865 | Spearphishing Attachment | attack-pattern--648f995e-9c3a-41e4-aeee-98bb41037426 | technique | targets | A0012 | Jump Host | x-mitre-asset--14932ed5-1098-4cc1-9f57-159ab7366787 | asset |  | relationship--3843dcca-62a2-4224-9241-05f981fa880a | 28 September 2023 | 28 September 2023
T0865 | Spearphishing Attachment | attack-pattern--648f995e-9c3a-41e4-aeee-98bb41037426 | technique | targets | A0001 | Workstation | x-mitre-asset--f1315d02-9118-4e3b-8cdf-4c2d3f77ce41 | asset |  | relationship--0d8e0324-ba8e-4712-a123-60377afe94da | 29 September 2023 | 29 September 2023
T0856 | Spoof Reporting Message | attack-pattern--8535b71e-3c12-4258-a4ab-40257a1becc4 | technique | targets | A0007 | Control Server | x-mitre-asset--ecb81a8b-022e-4529-a404-55cffca7d3a3 | asset |  | relationship--3212de2a-6635-4b95-aeb4-9c0744aed2ce | 28 September 2023 | 28 September 2023
T0856 | Spoof Reporting Message | attack-pattern--8535b71e-3c12-4258-a4ab-40257a1becc4 | technique | targets | A0009 | Data Gateway | x-mitre-asset--68388d4f-8138-420b-be2b-5a7dfe9ff6b4 | asset |  | relationship--69f4ed24-c2f7-49e1-99a2-350cc2795820 | 29 September 2023 | 29 September 2023
T0856 | Spoof Reporting Message | attack-pattern--8535b71e-3c12-4258-a4ab-40257a1becc4 | technique | targets | A0002 | Human-Machine Interface (HMI) | x-mitre-asset--3a95f7e4-4877-4967-b2e8-e287976c3e64 | asset |  | relationship--dd9abe36-1cee-4100-a94f-105d9678fd1f | 29 September 2023 | 29 September 2023
T0856 | Spoof Reporting Message | attack-pattern--8535b71e-3c12-4258-a4ab-40257a1becc4 | technique | targets | A0005 | Intelligent Electronic Device (IED) | x-mitre-asset--75f810ad-b678-4c57-b93b-fdc79bba0c04 | asset |  | relationship--e6af4cbd-1b2e-4733-be57-43a845f465eb | 28 September 2023 | 28 September 2023
T0856 | Spoof Reporting Message | attack-pattern--8535b71e-3c12-4258-a4ab-40257a1becc4 | technique | targets | A0003 | Programmable Logic Controller (PLC) | x-mitre-asset--986c455b-0f43-42b6-8360-33ac48bd9990 | asset |  | relationship--b352884f-2a60-41c6-b348-0bbb5859802a | 28 September 2023 | 28 September 2023
T0856 | Spoof Reporting Message | attack-pattern--8535b71e-3c12-4258-a4ab-40257a1becc4 | technique | targets | A0004 | Remote Terminal Unit (RTU) | x-mitre-asset--1769c499-55e5-462f-bab2-c39b8cd5ae32 | asset |  | relationship--f5c9f641-a498-46b5-9068-39502db53cfd | 28 September 2023 | 28 September 2023
T0856 | Spoof Reporting Message | attack-pattern--8535b71e-3c12-4258-a4ab-40257a1becc4 | technique | targets | A0010 | Safety Controller | x-mitre-asset--69d1b1ef-e918-4cfd-9a98-29debd04cb32 | asset |  | relationship--bf5356b1-d00e-43c3-ba92-ae504a737d76 | 29 September 2023 | 29 September 2023
T0869 | Standard Application Layer Protocol | attack-pattern--e076cca8-2f08-45c9-aff7-ea5ac798b387 | technique | targets | A0008 | Application Server | x-mitre-asset--973bc51e-c41e-4cec-ac03-9389c71f3d0d | asset |  | relationship--7b1e00af-11fb-4862-a193-55dc9b6652c0 | 29 September 2023 | 29 September 2023
T0869 | Standard Application Layer Protocol | attack-pattern--e076cca8-2f08-45c9-aff7-ea5ac798b387 | technique | targets | A0007 | Control Server | x-mitre-asset--ecb81a8b-022e-4529-a404-55cffca7d3a3 | asset |  | relationship--5131c799-517c-4bad-ba97-46ad7de956e7 | 28 September 2023 | 28 September 2023
T0869 | Standard Application Layer Protocol | attack-pattern--e076cca8-2f08-45c9-aff7-ea5ac798b387 | technique | targets | A0009 | Data Gateway | x-mitre-asset--68388d4f-8138-420b-be2b-5a7dfe9ff6b4 | asset |  | relationship--5425d1cd-8840-4640-90a3-72f3bd7151bd | 29 September 2023 | 29 September 2023
T0869 | Standard Application Layer Protocol | attack-pattern--e076cca8-2f08-45c9-aff7-ea5ac798b387 | technique | targets | A0006 | Data Historian | x-mitre-asset--e2c3336a-dd93-44d6-8246-f93cf132c499 | asset |  | relationship--ba496af3-2d99-4c2b-8ce0-20388f5d632c | 28 September 2023 | 28 September 2023
T0869 | Standard Application Layer Protocol | attack-pattern--e076cca8-2f08-45c9-aff7-ea5ac798b387 | technique | targets | A0002 | Human-Machine Interface (HMI) | x-mitre-asset--3a95f7e4-4877-4967-b2e8-e287976c3e64 | asset |  | relationship--9f2926a2-596f-459e-827e-6fe2d4646efd | 29 September 2023 | 29 September 2023
T0869 | Standard Application Layer Protocol | attack-pattern--e076cca8-2f08-45c9-aff7-ea5ac798b387 | technique | targets | A0005 | Intelligent Electronic Device (IED) | x-mitre-asset--75f810ad-b678-4c57-b93b-fdc79bba0c04 | asset |  | relationship--22548926-29b4-4882-9878-633375489c0e | 28 September 2023 | 28 September 2023
T0869 | Standard Application Layer Protocol | attack-pattern--e076cca8-2f08-45c9-aff7-ea5ac798b387 | technique | targets | A0012 | Jump Host | x-mitre-asset--14932ed5-1098-4cc1-9f57-159ab7366787 | asset |  | relationship--39e5a489-f557-4130-a285-e0a82f40685c | 28 September 2023 | 28 September 2023
T0869 | Standard Application Layer Protocol | attack-pattern--e076cca8-2f08-45c9-aff7-ea5ac798b387 | technique | targets | A0003 | Programmable Logic Controller (PLC) | x-mitre-asset--986c455b-0f43-42b6-8360-33ac48bd9990 | asset |  | relationship--2ecf9476-b546-44ff-8547-4ca56cf7eeb8 | 28 September 2023 | 28 September 2023
T0869 | Standard Application Layer Protocol | attack-pattern--e076cca8-2f08-45c9-aff7-ea5ac798b387 | technique | targets | A0004 | Remote Terminal Unit (RTU) | x-mitre-asset--1769c499-55e5-462f-bab2-c39b8cd5ae32 | asset |  | relationship--df9f5a5b-0662-4904-8e57-bc25c244a6da | 28 September 2023 | 28 September 2023
T0869 | Standard Application Layer Protocol | attack-pattern--e076cca8-2f08-45c9-aff7-ea5ac798b387 | technique | targets | A0010 | Safety Controller | x-mitre-asset--69d1b1ef-e918-4cfd-9a98-29debd04cb32 | asset |  | relationship--b7344dfb-621b-4558-ab22-6c1f256ee746 | 29 September 2023 | 29 September 2023
T0869 | Standard Application Layer Protocol | attack-pattern--e076cca8-2f08-45c9-aff7-ea5ac798b387 | technique | targets | A0011 | Virtual Private Network (VPN) Server | x-mitre-asset--0804f037-a3b9-4715-98e1-9f73d19d6945 | asset |  | relationship--ebc9f35c-6f95-4bc0-b8b3-f9b515690fa0 | 29 September 2023 | 29 September 2023
T0869 | Standard Application Layer Protocol | attack-pattern--e076cca8-2f08-45c9-aff7-ea5ac798b387 | technique | targets | A0001 | Workstation | x-mitre-asset--f1315d02-9118-4e3b-8cdf-4c2d3f77ce41 | asset |  | relationship--7c433b29-0ad3-4574-990f-e3d6291e7f23 | 29 September 2023 | 29 September 2023
T0862 | Supply Chain Compromise | attack-pattern--5e0f75da-e108-4688-a6de-a4f07cc2cbe3 | technique | targets | A0008 | Application Server | x-mitre-asset--973bc51e-c41e-4cec-ac03-9389c71f3d0d | asset |  | relationship--943a9a5c-7826-451d-ac73-34353ea40595 | 29 September 2023 | 29 September 2023
T0862 | Supply Chain Compromise | attack-pattern--5e0f75da-e108-4688-a6de-a4f07cc2cbe3 | technique | targets | A0007 | Control Server | x-mitre-asset--ecb81a8b-022e-4529-a404-55cffca7d3a3 | asset |  | relationship--3f92c11b-f6e2-4c07-9913-9fa7469ba4fe | 28 September 2023 | 28 September 2023
T0862 | Supply Chain Compromise | attack-pattern--5e0f75da-e108-4688-a6de-a4f07cc2cbe3 | technique | targets | A0009 | Data Gateway | x-mitre-asset--68388d4f-8138-420b-be2b-5a7dfe9ff6b4 | asset |  | relationship--208fe57b-cf2e-4188-8a6f-77597cd60351 | 29 September 2023 | 29 September 2023
T0862 | Supply Chain Compromise | attack-pattern--5e0f75da-e108-4688-a6de-a4f07cc2cbe3 | technique | targets | A0006 | Data Historian | x-mitre-asset--e2c3336a-dd93-44d6-8246-f93cf132c499 | asset |  | relationship--0750563d-a86c-4822-ab9c-0f2d3c304c6e | 28 September 2023 | 28 September 2023
T0862 | Supply Chain Compromise | attack-pattern--5e0f75da-e108-4688-a6de-a4f07cc2cbe3 | technique | targets | A0013 | Field I/O | x-mitre-asset--2b676abd-8263-49ea-81a4-78a7e1f776fe | asset |  | relationship--fd3bc308-82cd-49c9-a41e-9b19ce04b3cd | 02 October 2023 | 02 October 2023
T0862 | Supply Chain Compromise | attack-pattern--5e0f75da-e108-4688-a6de-a4f07cc2cbe3 | technique | targets | A0002 | Human-Machine Interface (HMI) | x-mitre-asset--3a95f7e4-4877-4967-b2e8-e287976c3e64 | asset |  | relationship--da771d72-c778-4c9a-acb4-01b5fc3d36c0 | 29 September 2023 | 29 September 2023
T0862 | Supply Chain Compromise | attack-pattern--5e0f75da-e108-4688-a6de-a4f07cc2cbe3 | technique | targets | A0005 | Intelligent Electronic Device (IED) | x-mitre-asset--75f810ad-b678-4c57-b93b-fdc79bba0c04 | asset |  | relationship--f08d487a-7837-48f9-9301-fe0f9f144c92 | 28 September 2023 | 28 September 2023
T0862 | Supply Chain Compromise | attack-pattern--5e0f75da-e108-4688-a6de-a4f07cc2cbe3 | technique | targets | A0012 | Jump Host | x-mitre-asset--14932ed5-1098-4cc1-9f57-159ab7366787 | asset |  | relationship--5e324da5-0fee-4dac-b289-410d560e03e9 | 28 September 2023 | 28 September 2023
T0862 | Supply Chain Compromise | attack-pattern--5e0f75da-e108-4688-a6de-a4f07cc2cbe3 | technique | targets | A0003 | Programmable Logic Controller (PLC) | x-mitre-asset--986c455b-0f43-42b6-8360-33ac48bd9990 | asset |  | relationship--b411f748-a1e9-40c6-8eb3-72f2de4dab08 | 28 September 2023 | 28 September 2023
T0862 | Supply Chain Compromise | attack-pattern--5e0f75da-e108-4688-a6de-a4f07cc2cbe3 | technique | targets | A0004 | Remote Terminal Unit (RTU) | x-mitre-asset--1769c499-55e5-462f-bab2-c39b8cd5ae32 | asset |  | relationship--19df16da-8247-45ef-be13-ba58b1fb9c1c | 28 September 2023 | 28 September 2023
T0862 | Supply Chain Compromise | attack-pattern--5e0f75da-e108-4688-a6de-a4f07cc2cbe3 | technique | targets | A0010 | Safety Controller | x-mitre-asset--69d1b1ef-e918-4cfd-9a98-29debd04cb32 | asset |  | relationship--dead5325-7efe-4dcc-bf78-42b9190f74da | 29 September 2023 | 29 September 2023
T0862 | Supply Chain Compromise | attack-pattern--5e0f75da-e108-4688-a6de-a4f07cc2cbe3 | technique | targets | A0011 | Virtual Private Network (VPN) Server | x-mitre-asset--0804f037-a3b9-4715-98e1-9f73d19d6945 | asset |  | relationship--c1e051ab-0a11-4d29-b98f-aa442ab69553 | 29 September 2023 | 29 September 2023
T0862 | Supply Chain Compromise | attack-pattern--5e0f75da-e108-4688-a6de-a4f07cc2cbe3 | technique | targets | A0001 | Workstation | x-mitre-asset--f1315d02-9118-4e3b-8cdf-4c2d3f77ce41 | asset |  | relationship--d775a6ed-4a60-41f4-ac06-da86c27cd1de | 29 September 2023 | 29 September 2023
T0894 | System Binary Proxy Execution | attack-pattern--1c5cf58c-a34a-40d7-82f4-f987cdfc2b91 | technique | targets | A0008 | Application Server | x-mitre-asset--973bc51e-c41e-4cec-ac03-9389c71f3d0d | asset |  | relationship--73c358d5-f4ce-4ce5-aa3d-d2ede8aff148 | 25 March 2024 | 25 March 2024
T0894 | System Binary Proxy Execution | attack-pattern--1c5cf58c-a34a-40d7-82f4-f987cdfc2b91 | technique | targets | A0007 | Control Server | x-mitre-asset--ecb81a8b-022e-4529-a404-55cffca7d3a3 | asset |  | relationship--46e4cdd2-e8f0-46aa-9264-868815a05af9 | 25 March 2024 | 25 March 2024
T0894 | System Binary Proxy Execution | attack-pattern--1c5cf58c-a34a-40d7-82f4-f987cdfc2b91 | technique | targets | A0006 | Data Historian | x-mitre-asset--e2c3336a-dd93-44d6-8246-f93cf132c499 | asset |  | relationship--deb83319-bc5a-4b9b-a44a-bd369b899601 | 25 March 2024 | 25 March 2024
T0894 | System Binary Proxy Execution | attack-pattern--1c5cf58c-a34a-40d7-82f4-f987cdfc2b91 | technique | targets | A0002 | Human-Machine Interface (HMI) | x-mitre-asset--3a95f7e4-4877-4967-b2e8-e287976c3e64 | asset |  | relationship--bad056aa-b8a6-4c4c-9bfa-bcc518872341 | 25 March 2024 | 25 March 2024
T0894 | System Binary Proxy Execution | attack-pattern--1c5cf58c-a34a-40d7-82f4-f987cdfc2b91 | technique | targets | A0012 | Jump Host | x-mitre-asset--14932ed5-1098-4cc1-9f57-159ab7366787 | asset |  | relationship--41a109dd-11d9-4840-a38b-088fc790f45a | 25 March 2024 | 25 March 2024
T0894 | System Binary Proxy Execution | attack-pattern--1c5cf58c-a34a-40d7-82f4-f987cdfc2b91 | technique | targets | A0001 | Workstation | x-mitre-asset--f1315d02-9118-4e3b-8cdf-4c2d3f77ce41 | asset |  | relationship--80cf98bd-b7dc-45cf-91a6-4ab6b79a7f0b | 25 March 2024 | 25 March 2024
T0857 | System Firmware | attack-pattern--b9160e77-ea9e-4ba9-b1c8-53a3c466b13d | technique | targets | A0009 | Data Gateway | x-mitre-asset--68388d4f-8138-420b-be2b-5a7dfe9ff6b4 | asset |  | relationship--b4bb8bd7-8984-45de-888f-45c51ab157fa | 29 September 2023 | 29 September 2023
T0857 | System Firmware | attack-pattern--b9160e77-ea9e-4ba9-b1c8-53a3c466b13d | technique | targets | A0002 | Human-Machine Interface (HMI) | x-mitre-asset--3a95f7e4-4877-4967-b2e8-e287976c3e64 | asset |  | relationship--33e33c74-2f17-4bac-bbba-bf4f2a2035e5 | 29 September 2023 | 29 September 2023
T0857 | System Firmware | attack-pattern--b9160e77-ea9e-4ba9-b1c8-53a3c466b13d | technique | targets | A0005 | Intelligent Electronic Device (IED) | x-mitre-asset--75f810ad-b678-4c57-b93b-fdc79bba0c04 | asset |  | relationship--beafc44c-228f-4a7e-9d92-ac1b16d730e2 | 28 September 2023 | 28 September 2023
T0857 | System Firmware | attack-pattern--b9160e77-ea9e-4ba9-b1c8-53a3c466b13d | technique | targets | A0003 | Programmable Logic Controller (PLC) | x-mitre-asset--986c455b-0f43-42b6-8360-33ac48bd9990 | asset |  | relationship--4508bdef-9528-47ae-804c-bc59d1e694e7 | 28 September 2023 | 28 September 2023
T0857 | System Firmware | attack-pattern--b9160e77-ea9e-4ba9-b1c8-53a3c466b13d | technique | targets | A0004 | Remote Terminal Unit (RTU) | x-mitre-asset--1769c499-55e5-462f-bab2-c39b8cd5ae32 | asset |  | relationship--817ae105-3ddf-4766-9d26-ca1ec3c64eb6 | 28 September 2023 | 28 September 2023
T0857 | System Firmware | attack-pattern--b9160e77-ea9e-4ba9-b1c8-53a3c466b13d | technique | targets | A0010 | Safety Controller | x-mitre-asset--69d1b1ef-e918-4cfd-9a98-29debd04cb32 | asset |  | relationship--a45cec05-2d81-4db1-9267-db8be498e0d2 | 29 September 2023 | 29 September 2023
T0857 | System Firmware | attack-pattern--b9160e77-ea9e-4ba9-b1c8-53a3c466b13d | technique | targets | A0011 | Virtual Private Network (VPN) Server | x-mitre-asset--0804f037-a3b9-4715-98e1-9f73d19d6945 | asset |  | relationship--1fd49958-9695-4137-9aaa-57fde4b97cc8 | 29 September 2023 | 29 September 2023
T0864 | Transient Cyber Asset | attack-pattern--35392fb4-a31d-4c6a-b9f2-1c65b7f5e6b9 | technique | targets | A0001 | Workstation | x-mitre-asset--f1315d02-9118-4e3b-8cdf-4c2d3f77ce41 | asset |  | relationship--16b74b29-e3b3-49ff-9ff4-cd7ade0f8ff4 | 29 September 2023 | 29 September 2023
T0855 | Unauthorized Command Message | attack-pattern--40b300ba-f553-48bf-862e-9471b220d455 | technique | targets | A0007 | Control Server | x-mitre-asset--ecb81a8b-022e-4529-a404-55cffca7d3a3 | asset |  | relationship--af25cacc-6b1a-47d2-8e13-cb2a7e92b379 | 28 September 2023 | 28 September 2023
T0855 | Unauthorized Command Message | attack-pattern--40b300ba-f553-48bf-862e-9471b220d455 | technique | targets | A0002 | Human-Machine Interface (HMI) | x-mitre-asset--3a95f7e4-4877-4967-b2e8-e287976c3e64 | asset |  | relationship--c4718fa2-2592-44b0-87d0-f866c118a779 | 29 September 2023 | 29 September 2023
T0855 | Unauthorized Command Message | attack-pattern--40b300ba-f553-48bf-862e-9471b220d455 | technique | targets | A0005 | Intelligent Electronic Device (IED) | x-mitre-asset--75f810ad-b678-4c57-b93b-fdc79bba0c04 | asset |  | relationship--f7bdbc1f-d08c-48a0-a474-a79b91526138 | 28 September 2023 | 28 September 2023
T0855 | Unauthorized Command Message | attack-pattern--40b300ba-f553-48bf-862e-9471b220d455 | technique | targets | A0003 | Programmable Logic Controller (PLC) | x-mitre-asset--986c455b-0f43-42b6-8360-33ac48bd9990 | asset |  | relationship--22ba5443-ea49-4076-a666-722eb5352f70 | 28 September 2023 | 28 September 2023
T0855 | Unauthorized Command Message | attack-pattern--40b300ba-f553-48bf-862e-9471b220d455 | technique | targets | A0004 | Remote Terminal Unit (RTU) | x-mitre-asset--1769c499-55e5-462f-bab2-c39b8cd5ae32 | asset |  | relationship--9c0db354-c2d6-4db0-bb76-35ae66c01dd1 | 28 September 2023 | 28 September 2023
T0855 | Unauthorized Command Message | attack-pattern--40b300ba-f553-48bf-862e-9471b220d455 | technique | targets | A0010 | Safety Controller | x-mitre-asset--69d1b1ef-e918-4cfd-9a98-29debd04cb32 | asset |  | relationship--33bc3e6f-e8cb-40ea-8088-3de39e2490a7 | 29 September 2023 | 29 September 2023
T0863 | User Execution | attack-pattern--2736b752-4ec5-4421-a230-8977dea7649c | technique | targets | A0002 | Human-Machine Interface (HMI) | x-mitre-asset--3a95f7e4-4877-4967-b2e8-e287976c3e64 | asset |  | relationship--604e1830-11ac-4ccf-a1d0-b22b80c1b024 | 29 September 2023 | 29 September 2023
T0863 | User Execution | attack-pattern--2736b752-4ec5-4421-a230-8977dea7649c | technique | targets | A0012 | Jump Host | x-mitre-asset--14932ed5-1098-4cc1-9f57-159ab7366787 | asset |  | relationship--1c7df4f1-cee5-42c6-a974-29552552666f | 28 September 2023 | 28 September 2023
T0863 | User Execution | attack-pattern--2736b752-4ec5-4421-a230-8977dea7649c | technique | targets | A0001 | Workstation | x-mitre-asset--f1315d02-9118-4e3b-8cdf-4c2d3f77ce41 | asset |  | relationship--7bbe6ac7-d0fb-40e4-8537-bdded7173f07 | 29 September 2023 | 29 September 2023
T0859 | Valid Accounts | attack-pattern--cd2c76a4-5e23-4ca5-9c40-d5e0604f7101 | technique | targets | A0008 | Application Server | x-mitre-asset--973bc51e-c41e-4cec-ac03-9389c71f3d0d | asset |  | relationship--1a900ac4-c150-4b57-a899-990854b01d4b | 29 September 2023 | 29 September 2023
T0859 | Valid Accounts | attack-pattern--cd2c76a4-5e23-4ca5-9c40-d5e0604f7101 | technique | targets | A0007 | Control Server | x-mitre-asset--ecb81a8b-022e-4529-a404-55cffca7d3a3 | asset |  | relationship--c047df7c-3ed7-455f-8b13-14ced8e93fef | 28 September 2023 | 28 September 2023
T0859 | Valid Accounts | attack-pattern--cd2c76a4-5e23-4ca5-9c40-d5e0604f7101 | technique | targets | A0009 | Data Gateway | x-mitre-asset--68388d4f-8138-420b-be2b-5a7dfe9ff6b4 | asset |  | relationship--639148fb-d0a5-4a2f-b6a3-a5ceb83d620b | 29 September 2023 | 29 September 2023
T0859 | Valid Accounts | attack-pattern--cd2c76a4-5e23-4ca5-9c40-d5e0604f7101 | technique | targets | A0006 | Data Historian | x-mitre-asset--e2c3336a-dd93-44d6-8246-f93cf132c499 | asset |  | relationship--d03de729-9235-4ceb-a1c0-935e2088020b | 28 September 2023 | 28 September 2023
T0859 | Valid Accounts | attack-pattern--cd2c76a4-5e23-4ca5-9c40-d5e0604f7101 | technique | targets | A0013 | Field I/O | x-mitre-asset--2b676abd-8263-49ea-81a4-78a7e1f776fe | asset |  | relationship--1865830b-511d-4302-99f7-6143647a8e40 | 02 October 2023 | 02 October 2023
T0859 | Valid Accounts | attack-pattern--cd2c76a4-5e23-4ca5-9c40-d5e0604f7101 | technique | targets | A0002 | Human-Machine Interface (HMI) | x-mitre-asset--3a95f7e4-4877-4967-b2e8-e287976c3e64 | asset |  | relationship--9e98d88c-4138-4d0e-8db0-cddf956ab500 | 29 September 2023 | 29 September 2023
T0859 | Valid Accounts | attack-pattern--cd2c76a4-5e23-4ca5-9c40-d5e0604f7101 | technique | targets | A0005 | Intelligent Electronic Device (IED) | x-mitre-asset--75f810ad-b678-4c57-b93b-fdc79bba0c04 | asset |  | relationship--8ccd5f5c-420a-413b-81ef-5e40f401be95 | 28 September 2023 | 28 September 2023
T0859 | Valid Accounts | attack-pattern--cd2c76a4-5e23-4ca5-9c40-d5e0604f7101 | technique | targets | A0012 | Jump Host | x-mitre-asset--14932ed5-1098-4cc1-9f57-159ab7366787 | asset |  | relationship--15377914-bf08-4c7e-ab00-1e272e2f3c1a | 28 September 2023 | 28 September 2023
T0859 | Valid Accounts | attack-pattern--cd2c76a4-5e23-4ca5-9c40-d5e0604f7101 | technique | targets | A0003 | Programmable Logic Controller (PLC) | x-mitre-asset--986c455b-0f43-42b6-8360-33ac48bd9990 | asset |  | relationship--6f2ddada-d7df-4788-b5d1-9add185142e0 | 28 September 2023 | 28 September 2023
T0859 | Valid Accounts | attack-pattern--cd2c76a4-5e23-4ca5-9c40-d5e0604f7101 | technique | targets | A0004 | Remote Terminal Unit (RTU) | x-mitre-asset--1769c499-55e5-462f-bab2-c39b8cd5ae32 | asset |  | relationship--f691dde5-bb2d-411b-a381-b33e0ab673d6 | 28 September 2023 | 28 September 2023
T0859 | Valid Accounts | attack-pattern--cd2c76a4-5e23-4ca5-9c40-d5e0604f7101 | technique | targets | A0010 | Safety Controller | x-mitre-asset--69d1b1ef-e918-4cfd-9a98-29debd04cb32 | asset |  | relationship--07f11dc3-60d7-42d3-a4f0-82eba85dfe44 | 29 September 2023 | 29 September 2023
T0859 | Valid Accounts | attack-pattern--cd2c76a4-5e23-4ca5-9c40-d5e0604f7101 | technique | targets | A0011 | Virtual Private Network (VPN) Server | x-mitre-asset--0804f037-a3b9-4715-98e1-9f73d19d6945 | asset |  | relationship--c4a50132-a210-4093-878d-3d6df23ed26e | 29 September 2023 | 29 September 2023
T0859 | Valid Accounts | attack-pattern--cd2c76a4-5e23-4ca5-9c40-d5e0604f7101 | technique | targets | A0001 | Workstation | x-mitre-asset--f1315d02-9118-4e3b-8cdf-4c2d3f77ce41 | asset |  | relationship--c39be68a-e208-47ac-a7be-6eb6e84d6608 | 29 September 2023 | 29 September 2023
T0860 | Wireless Compromise | attack-pattern--2877063e-1851-48d2-bcc6-bc1d2733157e | technique | targets | A0013 | Field I/O | x-mitre-asset--2b676abd-8263-49ea-81a4-78a7e1f776fe | asset |  | relationship--0f5295ce-d705-4541-8dda-c569b126d103 | 02 October 2023 | 02 October 2023
T0860 | Wireless Compromise | attack-pattern--2877063e-1851-48d2-bcc6-bc1d2733157e | technique | targets | A0001 | Workstation | x-mitre-asset--f1315d02-9118-4e3b-8cdf-4c2d3f77ce41 | asset |  | relationship--4b853b7c-bc55-4599-b88d-d08d651526c0 | 29 September 2023 | 29 September 2023
T0887 | Wireless Sniffing | attack-pattern--0fe075d5-beac-4d02-b93e-0f874997db72 | technique | targets | A0013 | Field I/O | x-mitre-asset--2b676abd-8263-49ea-81a4-78a7e1f776fe | asset |  | relationship--1429cd78-4e2a-4898-a7d8-d01a0c465bd6 | 02 October 2023 | 02 October 2023
T0887 | Wireless Sniffing | attack-pattern--0fe075d5-beac-4d02-b93e-0f874997db72 | technique | targets | A0001 | Workstation | x-mitre-asset--f1315d02-9118-4e3b-8cdf-4c2d3f77ce41 | asset |  | relationship--bac1f95c-87bf-4939-bc1a-7727aad738f7 | 29 September 2023 | 29 September 2023

## citations
reference | citation | url
A G Foord, W G Gulland, C R Howard, T Kellacher, W H Smith 2004 | A G Foord, W G Gulland, C R Howard, T Kellacher, W H Smith 2004 APPLYING THE LATEST STANDARD FOR FUNCTIONAL SAFETY IEC 61511 Retrieved. 2020/09/17 | https://www.icheme.org/media/9906/xviii-paper-23.pdf
Aditya K Sood July 2019 | Aditya K Sood 2019, July Discovering and fingerprinting BACnet devices Retrieved. 2020/09/25 | https://www.helpnetsecurity.com/2019/07/10/bacnet-devices/
Andy Greenberg June 2017 | Andy Greenberg. (2017, June 28). How an Entire Nation Became Russia's Test Lab for Cyberwar. Retrieved September 27, 2023. | https://www.wired.com/story/russian-hackers-attack-ukraine/
Andy Greenburg June 2019 | Andy Greenburg 2019, June 20 Iranian Hackers Launch a New US-Targeted Campaign as Tensions Mount Retrieved. 2020/01/03 | https://www.wired.com/story/iran-hackers-us-phishing-tensions/
Anton Cherepanov | Anton Cherepanov BlackEnergy by the SSHBearDoor: attacks against Ukrainian news media and electric industry Retrieved. 2019/10/29 | https://www.welivesecurity.com/2016/01/03/blackenergy-sshbeardoor-details-2015-attacks-ukrainian-news-media-electric-industry/
Anton Cherepanov, ESET June 2017 | Anton Cherepanov, ESET 2017, June 12 Win32/Industroyer: A new threat for industrial control systems Retrieved. 2017/09/15 | https://www.welivesecurity.com/wp-content/uploads/2017/06/Win32_Industroyer.pdf
Bastille April 2017 | Bastille 2017, April 17 Dallas Siren Attack Retrieved. 2020/11/06 | https://www.bastille.net/blogs/2017/4/17/dallas-siren-attack
Ben Hunter and Fred Gutierrez July 2020 | Ben Hunter and Fred Gutierrez 2020, July 01 EKANS Ransomware Targeting OT ICS Systems Retrieved. 2021/04/12 | https://www.fortinet.com/blog/threat-research/ekans-ransomware-targeting-ot-ics-systems
Blake Johnson, Dan Caban, Marina Krotofil, Dan Scali, Nathan Brubaker, Christopher Glyer December 2017 | Blake Johnson, Dan Caban, Marina Krotofil, Dan Scali, Nathan Brubaker, Christopher Glyer 2017, December 14 Attackers Deploy New ICS Attack Framework TRITON and Cause Operational Disruption to Critical Infrastructure Retrieved. 2018/01/12 | https://www.fireeye.com/blog/threat-research/2017/12/attackers-deploy-new-ics-attack-framework-triton.html
Booz Allen Hamilton | Booz Allen Hamilton When The Lights Went Out Retrieved. 2019/10/22 | https://www.boozallen.com/content/dam/boozallen/documents/2016/09/ukraine-report-when-the-lights-went-out.pdf
Brubaker-Incontroller | Nathan Brubaker, Keith Lunden, Ken Proska, Muhammad Umair, Daniel Kapellmann Zafra, Corey Hildebrandt, Rob Caldwell. (2022, April 13). INCONTROLLER: New State-Sponsored Cyber Attack Tools Target Multiple Industrial Control Systems. Retrieved September 28, 2022. | https://www.mandiant.com/resources/incontroller-state-sponsored-ics-tool
CISA AA23-335A IRGC-Affiliated December 2023 | DHS/CISA. (2023, December 1). IRGC-Affiliated Cyber Actors Exploit PLCs in Multiple Sectors, Including U.S. Water and Wastewater Systems Facilities. Retrieved March 25, 2024. | https://www.cisa.gov/news-events/cybersecurity-advisories/aa23-335a
CISA June 2013 | CISA 2013, June Risks of Default Passwords on the Internet Retrieved. 2020/09/25 | https://us-cert.cisa.gov/ncas/alerts/TA13-175A
CISA March 2010 | CISA 2010, March 11 https://us-cert.cisa.gov/ncas/tips/ST05-003 Retrieved. 2020/09/25 | https://us-cert.cisa.gov/ncas/tips/ST05-003
CISA Unitronics November 2023 | DHS/CISA. (2023, November 28). Exploitation of Unitronics PLCs used in Water and Wastewater Systems. Retrieved March 25, 2024. | https://www.cisa.gov/news-events/alerts/2023/11/28/exploitation-unitronics-plcs-used-water-and-wastewater-systems
CISA-AA22-103A | DHS/CISA. (2022, May 25). Alert (AA22-103A) APT Cyber Tools Targeting ICS/SCADA Devices. Retrieved September 28, 2022. | https://www.cisa.gov/uscert/ncas/alerts/aa22-103a
Carl Hurd March 2019 | Carl Hurd 2019, March 26 VPNFilter Deep Dive Retrieved. 2019/03/28 | https://www.youtube.com/watch?v=yuZazP22rpI
Catalin Cimpanu April 2016 | Catalin Cimpanu 2016, April 26 Malware Shuts Down German Nuclear Power Plant on Chernobyl's 30th Anniversary Retrieved. 2019/10/14 | https://news.softpedia.com/news/on-chernobyl-s-30th-anniversary-malware-shuts-down-german-nuclear-power-plant-503429.shtml
Charles McLellan March 2016 | Charles McLellan. (2016, March 4). How hackers attacked Ukraine's power grid: Implications for Industrial IoT security. Retrieved September 27, 2023. | https://www.zdnet.com/article/how-hackers-attacked-ukraines-power-grid-implications-for-industrial-iot-security/
Chris Bing May 2018 | Chris Bing 2018, May 24 Trisis masterminds have expanded operations to target U.S. industrial firms Retrieved. 2020/01/03 | https://www.cyberscoop.com/xenotime-ics-cyber-attacks-trisis-dragos/
Claroty Fuxnet 2024 | Team82. (2024, April 12). Unpacking the Blackjack Group's Fuxnet Malware. Retrieved September 11, 2024. | https://claroty.com/team82/research/unpacking-the-blackjack-groups-fuxnet-malware
Colin Gray | Colin Gray D. Parsons and D. Wylie 2019, September Practical Industrial Control System (ICS) Cybersecurity: IT and OT Have Converged Discover and Defend Your Assets Retrieved. 2020/09/25 How SDN Can Improve Cybersecurity in OT Networks Retrieved. 2020/09/25 | https://cdn.selinc.com/assets/Literature/Publications/Technical%20Papers/6891_HowSDN_CG_20180720_Web2.pdf?v=20190312-231901
D. Parsons and D. Wylie September 2019 | D. Parsons and D. Wylie 2019, September Practical Industrial Control System (ICS) Cybersecurity: IT and OT Have Converged Discover and Defend Your Assets Retrieved. 2020/09/25 | https://www.csiac.org/journal-article/practical-industrial-control-system-ics-cybersecurity-it-and-ot-have-converged-discover-and-defend-your-assets/
DHS National Urban Security Technology Laboratory April 2019 | DHS National Urban Security Technology Laboratory 2019, April Radio Frequency Detection, Spectrum Analysis, and Direction Finding Equipment Retrieved. 2020/09/17 | https://www.dhs.gov/sites/default/files/saver-msr-rf-detection_cod-508_10july2019.pdf
DHS CISA February 2019 | DHS CISA 2019, February 27 MAR-17-352-01 HatManSafety System Targeted Malware (Update B) Retrieved. 2019/03/08 | https://ics-cert.us-cert.gov/sites/default/files/documents/MAR-17-352-01%20HatMan%20-%20Safety%20System%20Targeted%20Malware%20%28Update%20B%29.pdf
Daavid Hentunen, Antti Tikkanen June 2014 | Daavid Hentunen, Antti Tikkanen 2014, June 23 Havex Hunts For ICS/SCADA Systems Retrieved. 2019/04/01 | https://www.f-secure.com/weblog/archives/00002718.html
Dan Goodin March 2017 | Dan Goodin 2017, March Virtual machine escape fetches $105,000 at Pwn2Own hacking contest Retrieved. 2020/09/25 | https://arstechnica.com/information-technology/2017/03/hack-that-escapes-vm-by-exploiting-edge-browser-fetches-105000-at-pwn2own/
Daniel Kapellmann Zafra, Keith Lunden, Nathan Brubaker, Jeremy Kennelly July 2020 | Daniel Kapellmann Zafra, Keith Lunden, Nathan Brubaker, Jeremy Kennelly 2020, July 15 Ransomware Against the Machine: How Adversaries are Learning to Disrupt Industrial Production by Targeting IT and OT Retrieved. 2021/04/12 | https://www.fireeye.com/blog/threat-research/2020/02/ransomware-against-machine-learning-to-disrupt-industrial-production.html
Davey Winder June 2020 | Davey Winder 2020, June 10 Honda Hacked: Japanese Car Giant Confirms Cyber Attack On Global Operations Retrieved. 2021/04/12 | https://www.forbes.com/sites/daveywinder/2020/06/10/honda-hacked-japanese-car-giant-confirms-cyber-attack-on-global-operations-snake-ransomware/?sh=2725c35753ad
David Voreacos, Katherine Chinglinsky, Riley Griffin December 2019 | David Voreacos, Katherine Chinglinsky, Riley Griffin 2019, December 03 Merck Cyberattacks $1.3 Billion Question: Was It an Act of War? Retrieved. 2019/12/06 | https://www.bloomberg.com/news/features/2019-12-03/merck-cyberattack-s-1-3-billion-question-was-it-an-act-of-war
Department of Homeland Security October 2009 | Department of Homeland Security 2009, October Developing an Industrial Control Systems Cybersecurity Incident Response Capability Retrieved. 2020/09/17 | https://us-cert.cisa.gov/sites/default/files/recommended_practices/final-RP_ics_cybersecurity_incident_response_100609.pdf
Department of Homeland Security September 2016 | Department of Homeland Security 2016, September Retrieved. 2020/09/25 | https://us-cert.cisa.gov/sites/default/files/recommended_practices/NCCIC_ICS-CERT_Defense_in_Depth_2016_S508C.pdf
Dragos | Dragos Allanite Retrieved. 2019/10/27 | https://dragos.com/resource/allanite/
Dragos Crashoverride 2018 | Joe Slowik. (2018, October 12). Anatomy of an Attack: Detecting and Defeating CRASHOVERRIDE. Retrieved December 18, 2020. | https://www.dragos.com/wp-content/uploads/CRASHOVERRIDE2018.pdf
Dragos Inc. June 2017 | Dragos Inc. 2017, June 13 Industroyer - Dragos - 201706: Analysis of the Threat to Electic Grid Operations Retrieved. 2017/09/18 | https://dragos.com/blog/crashoverride/CrashOverride-01.pdf
Dragos October 2018 | Dragos 2018, October 12 Anatomy of an Attack: Detecting and Defeating CRASHOVERRIDE Retrieved. 2019/10/14 | https://dragos.com/wp-content/uploads/CRASHOVERRIDE2018.pdf
Dragos Threat Intelligence August 2019 | Dragos Threat Intelligence 2019, August Global Oil and Gas Cyber Threat Perspective Retrieved. 2020/01/03 | https://dragos.com/wp-content/uploads/Dragos-Oil-and-Gas-Threat-Perspective-2019.pdf
Dragos Threat Intelligence February 2020 | Dragos Threat Intelligence 2020, February 03 EKANS Ransomware and ICS Operations Retrieved. 2021/04/12 | https://www.dragos.com/blog/industry-news/ekans-ransomware-and-ics-operations/
Dragos-Pipedream | DRAGOS. (2022, April 13). Pipedream: Chernovite’s Emerging Malware Targeting Industrial Control Systems. Retrieved September 28, 2022. | https://hub.dragos.com/hubfs/116-Whitepapers/Dragos_ChernoviteWP_v2b.pdf?hsLang=en
Dwight Anderson 2014 | Dwight Anderson 2014 Protect Critical Infrastructure Systems With Whitelisting Retrieved. 2020/09/25 | https://www.sans.org/reading-room/whitepapers/ICS/protect-critical-infrastructure-systems-whitelisting-35312
ESET | ESET ACAD/Medre.A: 10000s of AutoCAD Designs Leaked in Suspected Industrial Espionage Retrieved. 2021/04/13 | https://www.welivesecurity.com/wp-content/uploads/200x/white-papers/ESET_ACAD_Medre_A_whitepaper.pdf
ESET Industroyer | Anton Cherepanov. (2017, June 12). Win32/Industroyer: A new threat for industrial controls systems. Retrieved December 18, 2020. | https://www.welivesecurity.com/wp-content/uploads/2017/06/Win32_Industroyer.pdf
ESET Research Whitepapers September 2018 | ESET Research Whitepapers 2018, September LOJAX First UEFI rootkit found in the wild, courtesy of the Sednit group Retrieved. 2020/09/25 | https://www.welivesecurity.com/wp-content/uploads/2018/09/ESET-LoJax.pdf
Eduard Kovacs March 2018 | Eduard Kovacs 2018, March 1 Five Threat Groups Target Industrial Systems: Dragos Retrieved. 2020/01/03 | https://www.securityweek.com/five-threat-groups-target-industrial-systems-dragos
Eduard Kovacs May 2018 | Eduard Kovacs 2018, May 21 Group linked to Shamoon attacks targeting ICS networks in Middle East and UK Retrieved September 12, 2024. | https://web.archive.org/web/20220120001230/https://www.cyberviser.com/2018/05/group-linked-to-shamoon-attacks-targeting-ics-networks-in-middle-east-and-uk/
Emerson Exchange | Emerson Exchange Increase Security with TPM, Secure Boot, and Trusted Boot Retrieved. 2020/09/25 | https://emersonexchange365.com/products/control-safety-systems/f/plc-pac-systems-industrial-computing-forum/8383/increase-security-with-tpm-secure-boot-and-trusted-boot
FireEye TEMP.Veles 2018 | FireEye Intelligence . (2018, October 23). TRITON Attribution: Russian Government-Owned Lab Most Likely Built Custom Intrusion Tools for TRITON Attackers. Retrieved April 16, 2019. | https://www.fireeye.com/blog/threat-research/2018/10/triton-attribution-russian-government-owned-lab-most-likely-built-tools.html
FireEye TRITON | Blake Johnson, Dan Caban, Marina Krotofil, Dan Scali, Nathan Brubaker, Christopher Glyer. (2017, December 14). Attackers Deploy New ICS Attack Framework "TRITON" and Cause Operational Disruption to Critical Infrastructure. Retrieved January 6, 2021. | https://www.fireeye.com/blog/threat-research/2017/12/attackers-deploy-new-ics-attack-framework-triton.html
FireEye TRITON 2018 | Miller, S. Reese, E. (2018, June 7). A Totally Tubular Treatise on TRITON and TriStation. Retrieved January 6, 2021. | https://www.fireeye.com/blog/threat-research/2018/06/totally-tubular-treatise-on-TRITON-and-tristation.html
FireEye TRITON Dec 2017 | Blake Johnson, Dan Caban, Marina Krotofil, Dan Scali, Nathan Brubaker, Christopher Glyer. (2017, December 14). Attackers Deploy New ICS Attack Framework “TRITON” and Cause Operational Disruption to Critical Infrastructure. Retrieved January 12, 2018. | https://www.fireeye.com/blog/threat-research/2017/12/attackers-deploy-new-ics-attack-framework-triton.html
Frank Bajak and Marc Levy December 2023 | Frank Bajak and Marc Levy. (2023, December 2). Breaches by Iran-affiliated hackers spanned multiple U.S. states, federal agencies say. Retrieved March 25, 2024. | https://apnews.com/article/hackers-iran-israel-water-utilities-critical-infrastructure-cisa-554b2aa969c8220016ab2ef94bd7635b
Gardiner, J., Cova, M., Nagaraja, S February 2014 | Gardiner, J., Cova, M., Nagaraja, S 2014, February Command & Control Understanding, Denying and Detecting Retrieved. 2016/04/20 | https://arxiv.org/ftp/arxiv/papers/1408/1408.1136.pdf
Hydro | Hydro Kevin Beaumont How Lockergoga took down Hydro ransomware used in targeted attacks aimed at big business Retrieved. 2019/10/16 Retrieved. 2019/10/16 | https://www.hydro.com/en/media/on-the-agenda/cyber-attack/
ICS CERT September 2018 | ICS CERT 2018, September 06 Advantech/Broadwin WebAccess RPC Vulnerability (Update B) Retrieved. 2019/12/05 | https://www.us-cert.gov/ics/advisories/ICSA-11-094-02B
ICS-CERT August 2018 | ICS-CERT 2018, August 22 Advisory (ICSA-14-178-01) Retrieved. 2019/04/01 | https://ics-cert.us-cert.gov/advisories/ICSA-14-178-01
ICS-CERT December 2014 | ICS-CERT 2014, December 10 ICS Alert (ICS-ALERT-14-281-01E) Ongoing Sophisticated Malware Campaign Compromising ICS (Update E) Retrieved. 2019/10/11 | https://www.us-cert.gov/ics/alerts/ICS-ALERT-14-281-01B
ICS-CERT December 2018 | ICS-CERT 2018, December 18 Advisory (ICSA-18-107-02) - Schneider Electric Triconex Tricon (Update B) Retrieved. 2019/03/08 | https://ics-cert.us-cert.gov/advisories/ICSA-18-107-02
ICS-CERT October 2017 | ICS-CERT 2017, October 21 Advanced Persistent Threat Activity Targeting Energy and Other Critical Infrastructure Sectors Retrieved. 2017/10/23 | https://www.us-cert.gov/ncas/alerts/TA17-293A
IEC February 2019 | IEC 2019, February Security for industrial automation and control systems - Part 4-2: Technical security requirements for IACS components Retrieved. 2020/09/25 | https://webstore.iec.ch/publication/34421
Industroyer2 ESET April 2022 | ESET. (2022, April 12). Industroyer2: Industroyer reloaded. Retrieved March 30, 2023. | https://www.welivesecurity.com/2022/04/12/industroyer2-industroyer-reloaded/
Industroyer2 Forescout July 2022 | Forescout. (2022, July 14). Industroyer2 and INCONTROLLER In-depth Technical Analysis of the Most Recent ICS-specific Malware. Retrieved March 30, 2023. | https://www.forescout.com/resources/industroyer2-and-incontroller-report/
Industroyer2 Mandiant April 2022 | Daniel Kapellmann Zafra, Raymond Leong, Chris Sistrunk, Ken Proska, Corey Hildebrandt, Keith Lunden, Nathan Brubaker. (2022, April 25). INDUSTROYER.V2: Old Malware Learns New Tricks. Retrieved March 30, 2023. | https://www.mandiant.com/resources/blog/industroyer-v2-old-malware-new-tricks
Intel | Intel ESET Research Whitepapers 2018, September LOJAX First UEFI rootkit found in the wild, courtesy of the Sednit group Retrieved. 2020/09/25 Intel Hardware-based Security Technologies for Intelligent Retail Devices Retrieved. 2020/09/25 | https://www.intel.com/content/dam/www/public/us/en/documents/white-papers/security-technologies-4th-gen-core-retail-paper.pdf
Jacqueline O'Leary et al. September 2017 | Jacqueline O'Leary et al. 2017, September 20 Insights into Iranian Cyber Espionage: APT33 Targets Aerospace and Energy Sectors and has Ties to Destructive Malware Retrieved. 2019/12/02 | https://www.fireeye.com/blog/threat-research/2017/09/apt33-insights-into-iranian-cyber-espionage.html
Jamie Tarabay and Katrina Manson December 2023 | Jamie Tarabay and Katrina Manson. (2023, December 22). Iranian-Linked Hacks Expose Failure to Safeguard US Water System. Retrieved March 25, 2024. | https://www.bloomberg.com/news/articles/2023-12-22/iranian-linked-hacks-expose-failure-to-safeguard-us-water-system
Jeff Jones May 2018 | Jeff Jones 2018, May 10 Dragos Releases Details on Suspected Russian Infrastructure Hacking Team ALLANITE Retrieved. 2020/01/03 | https://www.eisac.com/public-news-detail?id=115909
Joe Slowik April 2019 | Joe Slowik 2019, April 10 Implications of IT Ransomware for ICS Environments Retrieved. 2019/10/27 | https://dragos.com/blog/industry-news/implications-of-it-ransomware-for-ics-environments/
Joe Slowik August 2019 | Joe Slowik 2019, August 15 CRASHOVERRIDE: Reassessing the 2016 Ukraine Electric Power Event as a Protection-Focused Attack Retrieved. 2019/10/22 | https://dragos.com/wp-content/uploads/CRASHOVERRIDE.pdf
Jos Wetzels January 2018 | Jos Wetzels 2018, January 16 Analyzing the TRITON industrial malware Retrieved. 2019/10/22 | https://www.midnightbluelabs.com/blog/2018/1/16/analyzing-the-triton-industrial-malware
Josh Rinaldi April 2016 | Josh Rinaldi 2016, April Still a Thrill: OPC UA Device Discovery Retrieved. 2020/09/25 | https://www.rtautomation.com/rtas-blog/still-a-thrill-opc-ua-device-discovery/
Julian Rrushi, Hassan Farhangi, Clay Howey, Kelly Carmichael, Joey Dabell December 2015 | Julian Rrushi, Hassan Farhangi, Clay Howey, Kelly Carmichael, Joey Dabell 2015, December 08 A Quantitative Evaluation of the Target Selection of Havex ICS Malware Plugin Retrieved. 2019/04/01 | https://pdfs.semanticscholar.org/18df/43ef1690b0fae15a36f770001160aefbc6c5.pdf
Junnosuke Yagi March 2017 | Junnosuke Yagi 2017, March 07 Trojan.Stonedrill Retrieved. 2019/12/05 | https://www.symantec.com/security-center/writeup/2017-030708-4403-99
Karen Scarfone; Paul Hoffman September 2009 | Karen Scarfone; Paul Hoffman 2009, September Guidelines on Firewalls and Firewall Policy Retrieved. 2020/09/25 | https://nvlpubs.nist.gov/nistpubs/Legacy/SP/nistspecialpublication800-41r1.pdf
Keith Stouffer May 2015 | Keith Stouffer 2015, May Guide to Industrial Control Systems (ICS) Security Retrieved. 2018/03/28 | https://nvlpubs.nist.gov/nistpubs/SpecialPublications/NIST.SP.800-82r2.pdf
Kelly Jackson Higgins | Kelly Jackson Higgins How a Manufacturing Firm Recovered from a Devastating Ransomware Attack Retrieved. 2019/11/03 | https://www.darkreading.com/attacks-breaches/how-a-manufacturing-firm-recovered-from-a-devastating-ransomware-attack/d/d-id/1334760
Kevin Beaumont | Kevin Beaumont How Lockergoga took down Hydro ransomware used in targeted attacks aimed at big business Retrieved. 2019/10/16 | https://doublepulsar.com/how-lockergoga-took-down-hydro-ransomware-used-in-targeted-attacks-aimed-at-big-business-c666551f5880
Kevin Savage and Branko Spasojevic | Kevin Savage and Branko Spasojevic W32.Flamer Retrieved. 2019/11/03 | https://web.archive.org/web/20190930124504/https://www.symantec.com/security-center/writeup/2012-052811-0308-99
Kyle Wilhoit | Kyle Wilhoit Daavid Hentunen, Antti Tikkanen 2014, June 23 Havex Hunts For ICS/SCADA Systems Retrieved. 2019/04/01 ICS Malware: Havex and Black Energy Retrieved. 2019/10/22 | https://www.youtube.com/watch?v=eywmb7UDODY&feature=youtu.be&t=939
Langer Stuxnet | Ralph Langner. (2013, November). To Kill a Centrifuge: A Technical Analysis of What Stuxnet's Creators Tried to Achieve. Retrieved December 7, 2020. | https://www.langner.com/wp-content/uploads/2017/03/to-kill-a-centrifuge.pdf
Langner November 2018 | Langner 2018, November Why Ethernet/IP changes the OT asset discovery game Retrieved. 2020/09/25 | https://www.langner.com/2018/11/why-ethernet-ip-changes-the-ot-asset-discovery-game/
Lisa Zahner December 2023 | Lisa Zahner. (2023, December 15). Hackers in Iran attack computer at Vero Utilities. Retrieved March 25, 2024. | https://veronews.com/2023/12/15/hackers-in-iran-attack-computer-at-vero-utilities/
M. Rentschler and H. Heine | M. Rentschler and H. Heine The Parallel Redundancy Protocol for industrial IP networks Retrieved. 2020/09/25 | https://ieeexplore.ieee.org/document/6505877
MDudek-ICS | MDudek-ICS TRISIS-TRITON-HATMAN Retrieved. 2019/11/03 | https://github.com/MDudek-ICS/TRISIS-TRITON-HATMAN/tree/master/decompiled_code/library
MITRE June 2020 | MITRE 2020, June CWE CATEGORY: 7PK - API Abuse Retrieved. 2020/09/25 | https://cwe.mitre.org/data/definitions/227.html
Mandiant-Sandworm-Ukraine-2022 | Ken Proska, John Wolfram, Jared Wilson, Dan Black, Keith Lunden, Daniel Kapellmann Zafra, Nathan Brubaker, Tyler Mclellan, Chris Sistrunk. (2023, November 9). Sandworm Disrupts Power in Ukraine Using a Novel Attack Against Operational Technology. Retrieved March 28, 2024. | https://www.mandiant.com/resources/blog/sandworm-disrupts-power-ukraine-operational-technology
Marc-Etienne M.Lveill October 2017 | Marc-Etienne M.Lveill 2017, October 24 Bad Rabbit: NotPetya is back with improved ransomware Retrieved. 2019/10/27 | https://www.welivesecurity.com/2017/10/24/bad-rabbit-not-petya-back/
Marshall Abrams July 2008 | Marshall Abrams 2008, July 23 Malicious Control System Cyber Security Attack Case Study Maroochy Water Services, Australia Retrieved. 2018/03/27 | https://www.mitre.org/sites/default/files/pdf/08_1145.pdf
Max Heinemeyer February 2020 | Max Heinemeyer 2020, February 21 Post-mortem of a targeted Sodinokibi ransomware attack Retrieved. 2021/04/12 | https://www.darktrace.com/en/blog/post-mortem-of-a-targeted-sodinokibi-ransomware-attack/
McAfee Labs October 2019 | McAfee Labs 2019, October 02 McAfee ATR Analyzes Sodinokibi aka REvil Ransomware-as-a-Service What The Code Tells Us Retrieved. 2021/04/12 | https://www.mcafee.com/blogs/other-blogs/mcafee-labs/mcafee-atr-analyzes-sodinokibi-aka-revil-ransomware-as-a-service-what-the-code-tells-us
McCarthy, J et al. July 2018 | McCarthy, J et al. 2018, July NIST SP 1800-2 Identity and Access Management for Electric Utilities Retrieved. 2020/09/17 | https://doi.org/10.6028/NIST.SP.1800-2
Microsoft August 2018 | Microsoft 2018, August Implementing Least-Privilege Administrative Models Retrieved. 2020/09/25 | https://docs.microsoft.com/en-us/windows-server/identity/ad-ds/plan/security-best-practices/implementing-least-privilege-administrative-models
Microsoft February 2019 | Microsoft 2019, February Active Directory administrative tier model Retrieved. 2020/09/25 | https://docs.microsoft.com/en-us/windows-server/identity/securing-privileged-access/securing-privileged-access-reference-material#a-nameesaebmaesae-administrative-forest-design-approach
Microsoft May 2017 | Microsoft 2017, May Attractive Accounts for Credential Theft Retrieved. 2020/09/25 | https://docs.microsoft.com/en-us/windows-server/identity/ad-ds/plan/security-best-practices/attractive-accounts-for-credential-theft
Microsoft Security Response Center August 2017 | Microsoft Security Response Center 2017, August Moving Beyond EMET II Windows Defender Exploit Guard Retrieved. 2020/09/25 | https://msrc-blog.microsoft.com/2017/08/09/moving-beyond-emet-ii-windows-defender-exploit-guard/
N/A | N/A Trusted Platform Module (TPM) Summary Retrieved. 2020/09/25 | https://www.trustedcomputinggroup.org/wp-content/uploads/Trusted-Platform-Module-Summary_04292008.pdf
National Institute of Standards and Technology April 2013 | National Institute of Standards and Technology 2013, April Security and Privacy Controls for Federal Information Systems and Organizations Retrieved. 2020/09/17 | https://nvlpubs.nist.gov/nistpubs/SpecialPublications/NIST.SP.800-53r4.pdf
National Security Agency February 2016 | National Security Agency 2016, February Position Zero: Integrity Checking Windows-Based ICS/SCADA Systems Retrieved. 2020/09/25 | https://apps.nsa.gov/iaarchive/library/ia-guidance/security-configuration/industrial-control-systems/position-zero-integrity-checking-windows-based-ics-scada-systems.cfm
Nicolas Falliere, Liam O Murchu, Eric Chien February 2011 | Nicolas Falliere, Liam O Murchu, Eric Chien 2011, February W32.Stuxnet Dossier (Version 1.4) Retrieved. 2017/09/22 | https://www.wired.com/images_blogs/threatlevel/2011/02/Symantec-Stuxnet-Update-Feb-2011.pdf
North America Transmission Forum December 2019 | North America Transmission Forum 2019, December NATF Transient Cyber Asset Guidance Retrieved. 2020/09/25 | https://www.natf.net/docs/natf/documents/resources/security/natf-transient-cyber-asset-guidance.pdf
Novetta Threat Research Group February 2016 | Novetta Threat Research Group 2016, February 24 Operation Blockbuster: Unraveling the Long Thread of the Sony Attack Retrieved. 2016/02/25 | https://web.archive.org/web/20220707091904/https://www.operationblockbuster.com/wp-content/uploads/2016/02/Operation-Blockbuster-Report.pdf
OWASP | OWASP Top 10 Web Application Security Risks Retrieved. 2020/09/25 | https://owasp.org/www-project-top-ten/
Orkhan Mamedov, Fedor Sinitsyn, Anton Ivanov October 2017 | Orkhan Mamedov, Fedor Sinitsyn, Anton Ivanov 2017, October 27 Bad Rabbit Ransomware Retrieved. 2019/10/27 | https://securelist.com/bad-rabbit-ransomware/82851/
PLCTop20 Mar 2023 | PLC Security, Top 20 Community. (2021, June 15). Secure PLC Coding Practices: Top 20 version 1.0. Retrieved March 22, 2023. | https://plc-security.com/content/Top_20_Secure_PLC_Coding_Practices_V1.0.pdf
Robert A. Martin January 2021 | Robert A. Martin 2021, January TRUSTING OUR SUPPLY CHAINS: A COMPREHENSIVE DATA-DRIVEN APPROACH Retrieved. 2021/04/12 | https://www.mitre.org/sites/default/files/publications/pr-20-01465-37-trusting-our-supply-chains-a-comprehensive-data-driven-approach.pdf
Robert Falcone, Bryan Lee May 2016 | Robert Falcone, Bryan Lee 2016, May 26 The OilRig Campaign: Attacks on Saudi Arabian Organizations Deliver Helminth Backdoor Retrieved. 2019/11/19 | https://unit42.paloaltonetworks.com/the-oilrig-campaign-attacks-on-saudi-arabian-organizations-deliver-helminth-backdoor/
Schneider Electric January 2018 | Schneider Electric 2018, January 23 TRITON - Schneider Electric Analysis and Disclosure Retrieved. 2019/03/14 | https://www.youtube.com/watch?v=f09E75bWvkk&index=3&list=PL8OWO1qWXF4qYG19p7An4Vw3N2YZ86aRS&t=0s
Schweitzer Engineering Laboratories August 2015 | Schweitzer Engineering Laboratories 2015, August Understanding When to Use LDAP or RADIUS for Centralized Authentication Retrieved. 2020/09/25 | https://cdn.selinc.com/assets/Literature/Publications/Application%20Notes/AN2015-08_20150817.pdf?
SecureWorks September 2019 | SecureWorks 2019, September 24 REvil/Sodinokibi Ransomware Retrieved. 2021/04/12 | https://www.secureworks.com/research/revil-sodinokibi-ransomware
Selena Larson, Camille Singleton December 2020 | Selena Larson, Camille Singleton 2020, December RANSOMWARE IN ICS ENVIRONMENTS Retrieved. 2021/04/12 | https://f.hubspotusercontent10.net/hubfs/5943619/Whitepaper-Downloads/Ransomware_in_ICS_Environments_Whitepaper_10_12_20.pdf?utm_referrer=https%3A%2F%2Fwww.dragos.com%2Fresource%2Fransomware-in-ics-environments%2F
Spenneberg, Ralf, Maik Brggemann, and Hendrik Schwartke March 2016 | Spenneberg, Ralf, Maik Brggemann, and Hendrik Schwartke 2016, March 31 Plc-blaster: A worm living solely in the plc. Retrieved. 2017/09/19 | https://www.blackhat.com/docs/asia-16/materials/asia-16-Spenneberg-PLC-Blaster-A-Worm-Living-Solely-In-The-PLC-wp.pdf
Symantec | Symantec W32.Duqu The precursor to the next Stuxnet Retrieved. 2019/11/03 | https://docs.broadcom.com/doc/w32-duqu-11-en
Symantec June 2015 | Symantec 2015, June 30 Simple steps to protect yourself from the Conficker Worm Retrieved. 2019/12/05 | https://support.symantec.com/us/en/article.tech93179.html
Symantec March 2019 | Symantec 2019, March 27 Elfin: Relentless Espionage Group Targets Multiple Organizations in Saudi Arabia and U.S. Retrieved. 2019/12/02 | https://www.symantec.com/blogs/threat-intelligence/elfin-apt33-espionage
Symantec Security Response July 2014 | Symantec Security Response 2014, July 7 Dragonfly: Cyberespionage Attacks Against Energy Suppliers Retrieved. 2016/04/08 | https://docs.broadcom.com/doc/dragonfly_threat_against_western_energy_suppliers#:~:text=The%20attackers%2C%20known%20to%20Symantec,supply%20in%20the%20affected%20countries.
The Office of Nuclear Reactor Regulation | The Office of Nuclear Reactor Regulation Schneider Electric 2018, January 23 TRITON - Schneider Electric Analysis and Disclosure Retrieved. 2019/03/14 Triconex Topical Report 7286-545-1 Retrieved. 2018/05/30 | https://www.nrc.gov/docs/ML1209/ML120900890.pdf
Tom Fakterman August 2019 | Tom Fakterman 2019, August 05 Sodinokibi: The Crown Prince of Ransomware Retrieved. 2021/04/12 | https://www.cybereason.com/blog/the-sodinokibi-ransomware-attack
Triton-EENews-2017 | Blake Sobczak. (2019, March 7). The inside story of the world’s most dangerous malware. Retrieved March 25, 2024. | https://www.eenews.net/articles/the-inside-story-of-the-worlds-most-dangerous-malware/
Ukraine15 - EISAC - 201603 | Electricity Information Sharing and Analysis Center; SANS Industrial Control Systems. (2016, March 18). Analysis of the Cyber Attack on the Ukranian Power Grid: Defense Use Case. Retrieved March 27, 2018. | https://nsarchive.gwu.edu/sites/default/files/documents/3891751/SANS-and-Electricity-Information-Sharing-and.pdf
WPXI Aliquippa Water November 2023 | WPXI. (2023, November 27). Officials investigating cyberattack on Municipal Water Authority of Aliquippa. Retrieved March 25, 2024. | https://www.wpxi.com/news/local/officials-investigating-cyberattack-municipal-water-authority-aliquippa/K5A3BEW35RAXJPMNHNE35RZ7WA/
Wikipedia | Wikipedia Microsoft Security Response Center 2017, August Moving Beyond EMET II Windows Defender Exploit Guard Retrieved. 2020/09/25 Control-flow integrity Retrieved. 2020/09/25 | https://en.wikipedia.org/wiki/Control-flow_integrity
William Largent June 2018 | William Largent 2018, June 06 VPNFilter Update - VPNFilter exploits endpoints, targets new devices Retrieved. 2019/03/28 | https://blog.talosintelligence.com/2018/06/vpnfilter-update.html
Wylie-22 | Jimmy Wylie. (2022, August). Analyzing PIPEDREAM: Challenges in Testing an ICS Attack Toolkit. Defcon 30. | https://media.defcon.org/DEF%20CON%2030/DEF%20CON%2030%20presentations/Jimmy%20Wylie%20-%20Analyzing%20PIPEDREAM%20Challenges%20in%20testing%20an%20ICS%20attack%20toolkit.pdf
Bonnie Zhu, Anthony Joseph, Shankar Sastry 2011 | Bonnie Zhu, Anthony Joseph, Shankar Sastry 2011 A Taxonomy of Cyber Attacks on SCADA Systems Retrieved. 2018/01/12 | http://ieeexplore.ieee.org/stamp/stamp.jsp?tp=&arnumber=6142258
Electricity Information Sharing and Analysis Center; SANS Industrial Control Systems March 2016 | Electricity Information Sharing and Analysis Center; SANS Industrial Control Systems 2016, March 18 Analysis of the Cyber Attack on the Ukranian Power Grid: Defense Use Case Retrieved. 2018/03/27 | https://assets.contentstack.io/v3/assets/blt36c2e63521272fdc/blt6a77276749b76a40/607f235992f0063e5c070fff/E-ISAC_SANS_Ukraine_DUC_5%5b73%5d.pdf
Enterprise ATT&CK | Enterprise ATT&CK Enterprise ATT&CK Service Stop Retrieved. 2019/10/29 Service Stop Retrieved. 2019/10/29 | https://attack.mitre.org/techniques/T1489/
IEC February 2013 | IEC 2013, February 20 IEC 61131-3:2013 Programmable controllers - Part 3: Programming languages Retrieved. 2019/10/22 | https://webstore.iec.ch/publication/4552
Bastille April 2017 | Bastille 2017, April 17 Dallas Siren Attack Retrieved. 2020/11/06 | https://www.bastille.net/blogs/2017/4/17/dallas-siren-attack
Candell, R., Hany, M., Lee, K. B., Liu,Y., Quimby, J., Remley, K. April 2018 | Candell, R., Hany, M., Lee, K. B., Liu,Y., Quimby, J., Remley, K. 2018, April Guide to Industrial Wireless Systems Deployments Retrieved. 2020/12/01 | https://nvlpubs.nist.gov/nistpubs/ams/NIST.AMS.300-4.pdf
Gallagher, S. April 2017 | Gallagher, S. 2017, April 12 Pirate radio: Signal spoof set off Dallas emergency sirens, not network hack Retrieved. 2020/12/01 | https://arstechnica.com/information-technology/2017/04/dallas-siren-hack-used-radio-signals-to-spoof-alarm-says-city-manager/
Corero | Corero Industrial Control System (ICS) Security Retrieved. 2019/11/04 | https://www.corero.com/resources/files/whitepapers/cns_whitepaper_ics.pdf
Michael J. Assante and Robert M. Lee | Michael J. Assante and Robert M. Lee Corero Industrial Control System (ICS) Security Retrieved. 2019/11/04 The Industrial Control System Cyber Kill Chain Retrieved. 2019/11/04 | https://www.sans.org/reading-room/whitepapers/ICS/industrial-control-system-cyber-kill-chain-36297
Tyson Macaulay | Tyson Macaulay Michael J. Assante and Robert M. Lee Corero Industrial Control System (ICS) Security Retrieved. 2019/11/04 The Industrial Control System Cyber Kill Chain Retrieved. 2019/11/04 RIoT Control: Understanding and Managing Risks and the Internet of Things Retrieved. 2019/11/04 | https://books.google.com/books?id=oXIYBAAAQBAJ&pg=PA249&lpg=PA249&dq=loss+denial+manipulation+of+view&source=bl&ots=dV1uQ8IUff&sig=ACfU3U2NIwGjhg051D_Ytw6npyEk9xcf4w&hl=en&sa=X&ved=2ahUKEwj2wJ7y4tDlAhVmplkKHSTaDnQQ6AEwAHoECAgQAQ#v=onepage&q=loss%20denial%20manipulation%20of%20view&f=false
Bruce Schneier January 2008 | Bruce Schneier 2008, January 17 Hacking Polish Trams Retrieved. 2019/10/17 | https://www.schneier.com/blog/archives/2008/01/hacking_the_pol.html
John Bill May 2017 | John Bill 2017, May 12 Hacked Cyber Security Railways Retrieved. 2019/10/17 | https://www.londonreconnections.com/2017/hacked-cyber-security-railways/
Shelley Smith February 2008 | Shelley Smith 2008, February 12 Teen Hacker in Poland Plays Trains and Derails City Tram System Retrieved. 2019/10/17 | https://inhomelandsecurity.com/teen_hacker_in_poland_plays_tr/
Common Weakness Enumeration January 2019 | Common Weakness Enumeration 2019, January 03 CWE-400: Uncontrolled Resource Consumption Retrieved. 2019/03/14 | http://cwe.mitre.org/data/definitions/400.html
ICS-CERT April 2017 | ICS-CERT 2017, April 18 CS Alert (ICS-ALERT-17-102-01A) BrickerBot Permanent Denial-of-Service Attack Retrieved. 2019/10/24 | https://www.us-cert.gov/ics/alerts/ICS-ALERT-17-102-01A
ICS-CERT August 2018 | ICS-CERT 2018, August 27 Advisory (ICSA-15-202-01) - Siemens SIPROTEC Denial-of-Service Vulnerability Retrieved. 2019/03/14 | https://ics-cert.us-cert.gov/advisories/ICSA-15-202-01
MITRE March 2018 | MITRE 2018, March 22 CVE-2015-5374 Retrieved. 2019/03/14 | https://nvd.nist.gov/vuln/detail/CVE-2015-5374
GTFO split | GTFOBins. (2020, November 13). split. Retrieved April 18, 2022. | https://gtfobins.github.io/gtfobins/split/
LOLBAS Project | Oddvar Moe et al. (2022, February). Living Off The Land Binaries, Scripts and Libraries. Retrieved March 7, 2022. | https://github.com/LOLBAS-Project/LOLBAS#criteria
split man page | Torbjorn Granlund, Richard M. Stallman. (2020, March null). split(1) — Linux manual page. Retrieved March 25, 2022. | https://man7.org/linux/man-pages/man1/split.1.html
Enterprise ATT&CK January 2018 | Enterprise ATT&CK 2018, January 11 Command-Line Interface Retrieved. 2018/05/17 | https://attack.mitre.org/wiki/Technique/T1059
Dennis L. Sloatman September 2016 | Dennis L. Sloatman 2016, September 16 Understanding PLC Programming Methods and the Tag Database System Retrieved. 2017/12/19 | https://www.radioworld.com/industry/understanding-plc-programming-methods-and-the-tag-database-system
Booz Allen Hamilton | Booz Allen Hamilton When The Lights Went Out Retrieved. 2019/10/22 | https://www.boozallen.com/content/dam/boozallen/documents/2016/09/ukraine-report-when-the-lights-went-out.pdf
Daavid Hentunen, Antti Tikkanen June 2014 | Daavid Hentunen, Antti Tikkanen 2014, June 23 Havex Hunts For ICS/SCADA Systems Retrieved. 2019/04/01 | https://www.f-secure.com/weblog/archives/00002718.html
CISA AA21-201A Pipeline Intrusion July 2021 | Department of Justice (DOJ), DHS Cybersecurity & Infrastructure Security Agency (CISA) 2021, July 20 Chinese Gas Pipeline Intrusion Campaign, 2011 to 2013 Retrieved. 2021/10/08 | https://us-cert.cisa.gov/sites/default/files/publications/AA21-201A_Chinese_Gas_Pipeline_Intrusion_Campaign_2011_to_2013%20(1).pdf
Alexander Bolshev March 2014 | Alexander Bolshev 2014, March 11 S4x14: HART As An Attack Vector Retrieved. 2020/01/05 | https://www.slideshare.net/dgpeters/17-bolshev-1-13
Alexander Bolshev, Gleb Cherbov July 2014 | Alexander Bolshev, Gleb Cherbov 2014, July 08 ICSCorsair: How I will PWN your ERP through 4-20 mA current loop Retrieved. 2020/01/05 | https://www.blackhat.com/docs/us-14/materials/us-14-Bolshev-ICSCorsair-How-I-Will-PWN-Your-ERP-Through-4-20mA-Current-Loop-WP.pdf
Machine Information Systems 2007 | Machine Information Systems 2007 How PLCs Work Retrieved. 2021/01/28 | http://www.machine-information-systems.com/How_PLCs_Work.html
N.A. October 2017 | N.A. 2017, October What are the different operating modes in PLC? Retrieved. 2021/01/28 | https://forumautomation.com/t/what-are-the-different-operating-modes-in-plc/2489
Omron | Omron Machine Information Systems 2007 How PLCs Work Retrieved. 2021/01/28 PLC Different Operating Modes Retrieved. 2021/01/28 | https://www.omron-ap.com/service_support/FAQ/FAQ00002/index.asp#:~:text=In%20PROGRAM%20mode%2C%20the%20CPU,can%20be%20created%20or%20modified.
PLCgurus 2021 | PLCgurus 2021 PLC Basics Modes Of Operation Retrieved. 2021/01/28 | https://www.plcgurus.net/plc-basics/
Jos Wetzels, Marina Krotofil 2019 | Jos Wetzels, Marina Krotofil 2019 A Diet of Poisoned Fruit: Designing Implants & OT Payloads for ICS Embedded Devices Retrieved. 2019/11/01 | https://troopers.de/downloads/troopers19/TROOPERS19_NGI_IoT_diet_poisoned_fruit.pdf
Cybersecurity & Infrastructure Security Agency March 2018 | Cybersecurity & Infrastructure Security Agency 2018, March 15 Alert (TA18-074A) Russian Government Cyber Activity Targeting Energy and Other Critical Infrastructure Sectors Retrieved. 2019/10/11 | https://us-cert.cisa.gov/ncas/alerts/TA18-074A
North American Electric Reliability Corporation June 2021 | North American Electric Reliability Corporation 2021, June 28 Glossary of Terms Used in NERC Reliability Standards Retrieved. 2021/10/11 | https://www.nerc.com/pa/Stand/Glossary%20of%20Terms/Glossary_of_Terms.pdf
Dr. Kelvin T. Erickson December 2010 | Dr. Kelvin T. Erickson 2010, December Programmable logic controller hardware Retrieved. 2018/03/29 | https://www.isa.org/standards-and-publications/isa-publications/intech/2010/december/programmable-logic-controller-hardware/
Nanjundaiah, Vaidyanath | Nanjundaiah, Vaidyanath Dr. Kelvin T. Erickson 2010, December Programmable logic controller hardware Retrieved. 2018/03/29 PLC Ladder Logic Basics Retrieved. 2021/10/11 | https://www.ezautomation.net/industry-articles/plc-ladder-logic-basics.htm
Benjamin Freed March 2019 | Benjamin Freed 2019, March 13 Tornado sirens in Dallas suburbs deactivated after being hacked and set off Retrieved. 2020/11/06 | https://statescoop.com/tornado-sirens-in-dallas-suburbs-deactivated-after-being-hacked-and-set-off/
Zack Whittaker April 2017 | Zack Whittaker 2017, April 12 Dallas' emergency sirens were hacked with a rogue radio signal Retrieved. 2020/11/06 | https://www.zdnet.com/article/experts-think-they-know-how-dallas-emergency-sirens-were-hacked/
Spenneberg, Ralf 2016 | Spenneberg, Ralf 2016 PLC-Blaster Retrieved. 2019/06/06 | https://www.blackhat.com/docs/asia-16/materials/asia-16-Spenneberg-PLC-Blaster-A-Worm-Living-Solely-In-The-PLC.pdf
Control Global May 2019 | Control Global 2019, May 29 Yokogawa announcement warns of counterfeit transmitters Retrieved. 2021/04/09 | https://www.controlglobal.com/industrynews/2019/yokogawa-announcement-warns-of-counterfeit-transmitters/
Colonial Pipeline Company May 2021 | Colonial Pipeline Company 2021, May Media Statement Update: Colonial Pipeline System Disruption Retrieved. 2021/10/08 | https://www.colpipe.com/news/press-releases/media-statement-colonial-pipeline-system-disruption
Lion Corporation June 2020 | Lion Corporation 2020, June 26 Lion Cyber incident update: 26 June 2020 Retrieved. 2021/10/08 | https://lionco.com/2020/06/26/lion-update-re-cyber-issue/
Paganini, Pierluigi June 2020 | Paganini, Pierluigi 2020, June 14 Ransomware attack disrupts operations at Australian beverage company Lion Retrieved. 2021/10/08 | https://securityaffairs.co/wordpress/104749/cyber-crime/ransomware-attack-hit-lion.html
Enterprise ATT&CK October 2019 | Enterprise ATT&CK 2019, October 25 Spearphishing Attachment Retrieved. 2019/10/25 | https://attack.mitre.org/techniques/T1193/
BSI State of IT Security 2014 | Bundesamt fr Sicherheit in der Informationstechnik (BSI) (German Federal Office for Information Security) 2014 Die Lage der IT-Sicherheit in Deutschland 2014 (The State of IT Security in Germany) Retrieved. 2019/10/30 | https://www.bsi.bund.de/SharedDocs/Downloads/EN/BSI/Publications/Securitysituation/IT-Security-Situation-in-Germany-2014.pdf?__blob=publicationFile&v=3
Joe Slowik April 2019 | Joe Slowik 2019, April 10 Implications of IT Ransomware for ICS Environments Retrieved. 2019/10/27 | https://dragos.com/blog/industry-news/implications-of-it-ransomware-for-ics-environments/
Keith Stouffer May 2015 | Keith Stouffer 2015, May Guide to Industrial Control Systems (ICS) Security Retrieved. 2018/03/28 | https://nvlpubs.nist.gov/nistpubs/SpecialPublications/NIST.SP.800-82r2.pdf
Daniel Oakley, Travis Smith, Tripwire | Daniel Oakley, Travis Smith, Tripwire Retrieved. 2018/05/30 | https://attack.mitre.org/wiki/Technique/T1133
Gabriel Sanchez October 2017 | Gabriel Sanchez 2017, October Man-In-The-Middle Attack Against Modbus TCP Illustrated with Wireshark Retrieved. 2020/01/05 | https://www.sans.org/reading-room/whitepapers/ICS/man-in-the-middle-attack-modbus-tcp-illustrated-wireshark-38095
Nicolas Falliere, Liam O Murchu, Eric Chien February 2011 | Nicolas Falliere, Liam O Murchu, Eric Chien 2011, February W32.Stuxnet Dossier (Version 1.4) Retrieved. 2017/09/22 | https://www.wired.com/images_blogs/threatlevel/2011/02/Symantec-Stuxnet-Update-Feb-2011.pdf
The MITRE Corporation May 2017 | The MITRE Corporation 2017, May 31 ATT&CK T1106: Native API Retrieved. 2021/04/26 | https://attack.mitre.org/techniques/T1106/
Mark Thompson March 2016 | Mark Thompson 2016, March 24 Iranian Cyber Attack on New York Dam Shows Future of War Retrieved. 2019/11/07 | https://time.com/4270728/iran-cyber-attack-dam-fbi/
Danny Yadron December 2015 | Danny Yadron 2015, December 20 Iranian Hackers Infiltrated New York Dam in 2013 Retrieved. 2019/11/07 | https://www.wsj.com/articles/iranian-hackers-infiltrated-new-york-dam-in-2013-1450662559
Basnight, Zachry, et al. | Basnight, Zachry, et al. 2013 Retrieved. 2017/10/17 | http://www.sciencedirect.com/science/article/pii/S1874548213000231
BBC April 2016 | BBC 2016, April 28 German nuclear plant hit by computer viruses Retrieved. 2019/10/14 | https://www.bbc.com/news/technology-36158606
Catalin Cimpanu April 2016 | Catalin Cimpanu 2016, April 26 Malware Shuts Down German Nuclear Power Plant on Chernobyl's 30th Anniversary Retrieved. 2019/10/14 | https://news.softpedia.com/news/on-chernobyl-s-30th-anniversary-malware-shuts-down-german-nuclear-power-plant-503429.shtml
Christoph Steitz, Eric Auchard April 2016 | Christoph Steitz, Eric Auchard 2016, April 26 German nuclear plant infected with computer viruses, operator says Retrieved. 2019/10/14 | https://www.reuters.com/article/us-nuclearpower-cyber-germany/german-nuclear-plant-infected-with-computer-viruses-operator-says-idUSKCN0XN2OS
Dark Reading Staff April 2016 | Dark Reading Staff 2016, April 28 German Nuclear Power Plant Infected With Malware Retrieved. 2019/10/14 | https://www.darkreading.com/endpoint/german-nuclear-power-plant-infected-with-malware/d/d-id/1325298
ESET April 2016 | ESET 2016, April 28 Malware found at a German nuclear power plant Retrieved. 2019/10/14 | https://www.welivesecurity.com/2016/04/28/malware-found-german-nuclear-power-plant/
Kernkraftwerk Gundremmingen April 2016 | Kernkraftwerk Gundremmingen 2016, April 25 Detektion von Bro-Schadsoftware an mehreren Rechnern Retrieved. 2019/10/14 | https://www.kkw-gundremmingen.de/presse.php?id=571
Lee Mathews April 2016 | Lee Mathews 2016, April 27 German nuclear plant found riddled with Conficker, other viruses Retrieved. 2019/10/14 | https://www.geek.com/apps/german-nuclear-plant-found-riddled-with-conficker-other-viruses-1653415/
Peter Dockrill April 2016 | Peter Dockrill 2016, April 28 Multiple Computer Viruses Have Been Discovered in This German Nuclear Plant Retrieved. 2019/10/14 | https://www.sciencealert.com/multiple-computer-viruses-have-been-discovered-in-this-german-nuclear-plant
Sean Gallagher April 2016 | Sean Gallagher 2016, April 27 German nuclear plants fuel rod system swarming with old malware Retrieved. 2019/10/14 | https://arstechnica.com/information-technology/2016/04/german-nuclear-plants-fuel-rod-system-swarming-with-old-malware/
Trend Micro April 2016 | Trend Micro 2016, April 27 Malware Discovered in German Nuclear Power Plant Retrieved. 2019/10/14 | https://www.trendmicro.com/vinfo/us/security/news/cyber-attacks/malware-discovered-in-german-nuclear-power-plant
ICS-CERT October 2017 | ICS-CERT 2017, October 21 Advanced Persistent Threat Activity Targeting Energy and Other Critical Infrastructure Sectors Retrieved. 2017/10/23 | https://www.us-cert.gov/ncas/alerts/TA17-293A
The MITRE Corporation | The MITRE Corporation The MITRE Corporation ATT&CK T1068: Exploitation for Privilege Escalation Retrieved. 2021/04/12 ATT&CK T1068: Exploitation for Privilege Escalation Retrieved. 2021/04/12 | https://attack.mitre.org/techniques/T1068/
Blake Johnson, Dan Caban, Marina Krotofil, Dan Scali, Nathan Brubaker, Christopher Glyer December 2017 | Blake Johnson, Dan Caban, Marina Krotofil, Dan Scali, Nathan Brubaker, Christopher Glyer 2017, December 14 Attackers Deploy New ICS Attack Framework TRITON and Cause Operational Disruption to Critical Infrastructure Retrieved. 2018/01/12 | https://www.fireeye.com/blog/threat-research/2017/12/attackers-deploy-new-ics-attack-framework-triton.html
Dragos December 2017 | Dragos 2017, December 13 TRISIS Malware Analysis of Safety System Targeted Malware Retrieved. 2018/01/12 | https://dragos.com/blog/trisis/TRISIS-01.pdf
Mark Loveless April 2017 | Mark Loveless 2017, April 11 THE DALLAS COUNTY SIREN HACK Retrieved. 2020/11/06 | https://duo.com/decipher/the-dallas-county-siren-hack
Beckhoff | Beckhoff TwinCAT 3 Source Control: Project Files Retrieved. 2019/11/21 | https://infosys.beckhoff.com/english.php?content=../content/1033/tc3_sourcecontrol/18014398915785483.html&id=
PLCdev | PLCdev Nicolas Falliere, Liam O Murchu, Eric Chien 2011, February W32.Stuxnet Dossier (Version 1.4) Retrieved. 2017/09/22 Siemens SIMATIC Step 7 Programmer's Handbook Retrieved. 2019/11/21 | http://www.plcdev.com/book/export/html/373
MITRE | MITRE System Network Connections Discovery Retrieved. 2018/05/31 | https://attack.mitre.org/wiki/Technique/T1049
Netstat | Wikipedia. (n.d.). Netstat. Retrieved May 23, 2022. | https://en.wikipedia.org/wiki/Netstat
Daniel Peck, Dale Peterson January 2009 | Daniel Peck, Dale Peterson 2009, January 28 Leveraging Ethernet Card Vulnerabilities in Field Devices Retrieved. 2017/12/19 | https://www.researchgate.net/publication/228849043_Leveraging_ethernet_card_vulnerabilities_in_field_devices
NCCIC January 2014 | NCCIC 2014, January 1 Internet Accessible Control Systems At Risk Retrieved. 2019/11/07 | https://www.us-cert.gov/sites/default/files/Monitors/ICS-CERT_Monitor_Jan-April2014.pdf
Stephen Hilt, Federico Maggi, Charles Perine, Lord Remorin, Martin Rsler, and Rainer Vosseler | Stephen Hilt, Federico Maggi, Charles Perine, Lord Remorin, Martin Rsler, and Rainer Vosseler Mark Thompson 2016, March 24 Iranian Cyber Attack on New York Dam Shows Future of War Retrieved. 2019/11/07 Caught in the Act: Running a Realistic Factory Honeypot to Capture Real Threats Retrieved. 2021/04/12 | https://documents.trendmicro.com/assets/white_papers/wp-caught-in-the-act-running-a-realistic-factory-honeypot-to-capture-real-threats.pdf
German BAS Lockout Dec 2021 | Kelly Jackson Higgins. (2021, December 20). Lights Out: Cyberattacks Shut Down Building Automation Systems. Retrieved March 30, 2023. | https://www.darkreading.com/attacks-breaches/lights-out-cyberattacks-shut-down-building-automation-systems